# CLALLAM COUNTY

CLALLAM BAY / SEKIU

GENERAL SEWER / FACILITIES PLAN

AMENDMENT

Prepared By:

WILSON ENGINEERING, LLC

805 Dupont Street, Suite #7

Bellingham, Washington 98225

(360) 733-6100

Project # 2020-105

W:\2021\2021-044 CLALLAM COUNTY WWTP VALUE PLANNING\REPORT AMENDMENT\REPORT AMENDMENT 2-13-23.DOCX

February 2023

CLALLAM BAY / SEKIU

GENERAL SEWER / FACILITIES PLAN

AMENDMENT

Prepared for:

Clallam County

By:

Wilson Engineering, LLC

# Table of Contents

Table of Contents	v

List of Tables	ix

List of Figures	xi

List of Appendices	xii

1.0 - INTRODUCTION	1

Purpose	1

Background	1

2.0 – LAND USE, POPULATION PROJECTIONS, AND SERVICE AREA CHARACTERISTICS	2

Sewer Service Areas	2

Natural Environment	2

Water System	2

Planning Period	2

Land Use, Zoning, and Population	2

Sewer Connections	2

Industries in the Sewer Service Area	2

3.0 - REGULATORY REQUIREMENTS	3

Federal Clean Water Act – NPDES	3

Puget Sound Nutrient General Permit	3

Federal Endangered Species Act	4

National Environmental Policy Act (NEPA)	4

State Environmental Review Process (SERP)	4

State Environmental Policy Act (SEPA)	5

Investment Grade Efficiency Audit (IGEA)	5

Cost and Effectiveness Analysis (CEA)	5

Archaeological and Cultural Resources Survey	6

Stormwater Permitting in the State of Washington	6

Shoreline Permit	6

Hydraulic Project Approval	6

Clallam County Codes	7

Regulatory Summary	7

Funding 	8

Department of Ecology – CWSRF	8

USDA – Rural Development – Water and Waste Disposal Loans and Grants	8

Department of Commerce – Community Development Block Grant	8

Rural Community Assistance Corporation	8

4.0 – EXISTING FACILITIES	10

Wastewater Collection System	10

Wastewater Treatment Plants	10

5.0 - EXISTING AND PROJECTED WASTEWATER FLOWS AND CHARACTERISTICS	11

Existing Wastewater Flows	12

Annual Average	12

Monthly Average	12

Peak Month and Peak Day	14

Existing Wastewater Loadings (BOD5, TSS)	15

Existing Nutrient Concentrations	16

Clallam Bay Corrections Center Flows and Loadings	18

Future Projected Wastewater Flows	19

Future Projected Wastewater Loadings (BOD, TSS)	20

6.0 - COLLECTION SYSTEM EVALUATION	22

I/I Analysis	22

Flow Monitoring	22

Smoke Testing	22

Manhole Inspections	22

CCTV Inspection	22

Hydraulic Model	22

Lift Station Capacity Analysis	22

Force Main Capacity Evaluation	22

Field Observations	23

Collection System Improvement Summary	23

Lift Station Improvement Summary	24

WWTP Upgrade-Related Capital Improvement Summary	24

7.0 - Wastewater Treatment Facility Evaluation	26

Historical Plant Performance	26

Clallam Bay WWTP	26

Sekiu WWTP	26

Permits	26

Clallam Bay WWTP NPDES Discharge Permits	26

Sekiu WWTP NPDES Discharge Permits	26

Nutrient Removal	26

Facility Evaluation at Projected Design Criteria	26

Influent Screening and Grit Removal	26

Influent Flow Meter	26

Primary Clarifiers	27

Rotating Biological Contactor Basins (RBC Basin)	27

Secondary Clarifiers	27

Aeration Blowers	27

UV Disinfection System	27

Aerobic Digesters	27

Non-Potable Water System	27

Electrical, Control System, and Telemetry	27

Outfall	27

Evaluation of WWTP Alternatives	27

Design Criteria	27

WWTP Alternatives	32

Alternative 1 – Biolac at Corrections Center	36

Alternative 2 – Aeromod at New Lot in Sekiu	36

Alternative 3 – Aeromod at Existing Sekiu WWTP	38

Alternative 4 – Aeromod at Corrections Center	40

Summary of Alternatives	41

Treatment Alternative Cost Estimates	41

8.0 - CAPITAL IMPROVEMENT PROGRAM	44

Sewer System Capital Improvements	44

Lift Station Capital Improvements	44

Wastewater Treatment Plant Capital Improvements	44

WWTP Recommended Alternative	44

Future Nutrient Effluent Limits	45

Outfall Improvements	45

Staffing and Testing Requirements	45

Biosolids Handling	46

Construction Phasing	46

WWTP Upgrade Costs	47

Capital Improvements Plan Schedule	47

9.0 - FINANCIAL ANALYSIS	48

Financial Status of Existing Clallam Bay – Sekiu Wastewater Treatment Plant	48

Projected Expenses, Revenues, and Capital Reserves	48

Capital Improvement Financing	48

Public Financing Sources	48

# List of Tables

Table 2-1:  SERP Timing	4

Table 2-2:  Summary of Regulatory Requirements	7

Table 5-1:  Clallam Bay WWTP Annual Average Flow	12

Table 5-2:  Sekiu WWTP Annual Average Flow	12

Table 5-3:  Clallam Bay WWTP Monthly Average Flow	13

Table 5-4:  Sekiu WWTP Monthly Average Flow	13

Table 5-5:  Clallam Bay WWTP Peak Month and Peak Day Flows	14

Table 5-6:  Sekiu WWTP Peak Month and Peak Day Flows	14

Table 5-7:  Clallam Bay WWTP Influent BOD5 and TSS Loading	15

Table 5-8:  Clallam Bay WWTP Influent BOD Loading, Summer and Winter	15

Table 5-9:  Sekiu WWTP Influent BOD5 and TSS Loading	15

Table 5-10:  Sekiu WWTP Influent BOD5 Loading, Summer and Winter	15

Table 5-11: Clallam Bay WWTP Nutrient Concentrations	17

Table 5-12: Sekiu WWTP Nutrient Concentrations	17

Table 5-13:  Clallam Bay Corrections Center WWTP Annual Average Flow	18

Table 5-14:  Clallam Bay Corrections Center WWTP Peak Month and Peak Day Influent Flows	18

Table 5-15:  Clallam Bay Corrections Center WWTP Influent CBOD5 and TSS Loading	18

Table 5-16:  Clallam Bay Corrections Center WWTP Influent CBOD5 Loading, Summer and Winter	19

Table 5-17:  Clallam Bay and Sekiu UGA Population Projections	19

Table 5-18:  Clallam Bay WWTP Projected Flows	19

Table 5-19:  Sekiu WWTP Projected Flows	19

Table 5-20:  Clallam Bay Corrections Center WWTP Projected Flows	20

Table 5-21:  Clallam Bay WWTP Projected Loadings	20

Table 5-22:  Sekiu WWTP Projected Loadings	20

Table 6-12:  Collection System Improvement Projects	23

Table 6-13:  Collection System Improvement Projects	24

Table 6-14:  Capital Improvement Projects Required for WWTP Upgrade Alternatives	24

Table 7-1:  Clallam Current Permitted Influent Flow / Loading Limits	28

Table 7-2:  Sekiu Current Permitted Influent Flow / Loading Limits	28

Table 7-3:  Corrections Center Current Permitted Influent Flow / Loading Limits	28

Table 7-4: Clallam Bay Influent Flows and Loadings	28

Table 7-5: Sekiu Influent Flows and Loadings	29

Table 7-6:  Corrections Center Influent Flows and Loadings	29

Table 7-7: Sekiu and Corrections Center Combined Influent Flows and Loadings	30

Table 7-8: Sekiu and Clallam Bay Combined Influent Flows and Loadings	30

Table 7-9:  Combined (Sekiu, Clallam Bay and Corrrections Center) Influent Flows and Loadings	31

Table 7-10:  Effluent Design Criteria	31

Table 7-11:  Capital Improvement Projects Required for WWTP Alternatives	35

Table 7-12:  Alternative 2 Cost Estimates	37

Table 7-13:  Alternative 2 Site Layout Advantages and Disadvantages	38

Table 7-14:  Alternative 3 Cost Estimates	39

Table 7-15:  Alternative 3 Site Layout Advantages and Disadvantages	39

Table 7-16:  WWTP Alternatives Summary	41

Table 7-17:  Total Project Construction Cost Estimates for Alternatives	42

Table 7-18:  Overall 22-Year Life Cycle Cost Estimates for Alternatives	43

Table 8-1:  Biosolids Handling Costs	46

Table 8-2:  Cost Summary for Recommended WWTP Upgrade	47

# List of Figures

Figure 5-1: Clallam Bay Monthly Average Influent BOD5 (lb/day) 2018-2022	16

Figure 5-2: Sekiu Monthly Average Influent BOD5 (lb/day) 2018-2022	16

Figure 5-3: Clallam Bay WWTP Existing Peak Month Influent Loading and Flow 2018-2022.  Projected Peak Month Influent Flow and Loading 2023-2046.	21

Figure 5-4: Sekiu WWTP Existing Peak Month Influent Loading and Flow 2018-2022.  Projected Peak Month Influent Flow and Loading 2023-2046.	21

# List of Appendices

Appendix A.	figures and maps

Appendix B. 	wwtp alternatives exhibits

Appendix c.  	summary of grant & loan programs

appendix d.  	CAPITAL IMPROVEMENT PLAN

appendix e.   	PERMITS

appendix f.  	Cost estimates

appendix g.  	SEPA CHECKLIST and determination

appendix h.	calculations

# List of Abbreviations

| BOD5 | 5-Day Biochemical Oxygen Demand |
| --- | --- |
| CBOD5 | 5-Day Carbonaceous Biochemical Oxygen Demand |
| cu ft | cubic feet |
| DO | Dissolved Oxygen |
| ERU | Equivalent Residential Unit |
| F/M | Food to Microorganism Ratio |
| GMA | Growth Management Act |
| GPD | gallons per day |
| GPM | gallons per minute |
| HRT | Hydraulic Residence Time |
| IFAS | Integrated Fixed-Film Activated Sludge |
| kW | kilowatt |
| kW/hr | kilowatt-hour |
| lbs | pounds |
| MBR | Membrane Bioreactor |
| MCRT | Mean Cell Residence Time |
| mg/L | milligrams per liter |
| MGD | million gallons per day |
| MLE | Modified Ludzack-Ettinger (Process) |
| MLSS | Mixed Liquor Suspended Solids |
| MLVSS | Mixed Liquor Volatile Suspended Solids |
| MMDF | Maximum Month Daily Flow |
| psi | pounds per square inch |
| RAS | Return Activated Sludge |
| rpm | revolutions per minute |
| SCFM | standard cubic feet per minute |
| sq ft | square feet |
| STEP | Septic Tank Effluent Pumping (System) |
| SVI | Sludge Volume Index |
| TIN | Total Inorganic Nitrogen |
| TKN | Total Kjeldahl Nitrogen |
| TN | Total Nitrogen |
| TSS | Total Suspended Solids |
| VSS | Volatile Suspended Solids |
| WAS | Waste Activated Sludge |
| WWTP | Wastewater Treatment Plant |

# 1.0 - INTRODUCTION

### Purpose

This Amendment to the 2018 General Sewer and Wastewater Facilities Plan (2018 Plan) for the Clallam Bay and Sekiu area was prepared at the request of Clallam County and in accordance with the Washington State Department of Ecology (DOE) requirements as presented in WAC 173-240-050 and 173-240-060, and the sewer-water district planning requirements as presented in RCW 57.16. This report is an amendment to the 2018 General Sewer / Wastewater Facilities Plan prepared by Gray & Osborne, Inc.

The purpose of this Amendment is to provide an updated plan for required improvements to the existing wastewater treatment facility and collection system to address aging infrastructure & challenging equipment, future flow and loading capacity, future nutrient removal requirements, and current standards for redundancy and reliability. This report evaluates the area wastewater needs based on projected residential population growth and commercial and industrial demands on the treatment system through the year 2046.

This Amendment includes a schedule for the County to provide adequate sewer collection and treatment capacity in accordance with Washington DOE requirements.  In addition, this Amendment is intended to be used to apply for and receive either grants or loans from the Department of Ecology, USDA, CDBG, or other funding sources for Sewer Capital Improvement Projects.

### Background

This Amendment is the result of value engineering performed at the request of Clallam County.  Project costs estimated in the 2018 Plan were assumed to be extraordinarily high and value engineering was determined to be appropriate to find the most cost-effective solutions.

# 2.0 – LAND USE, POPULATION PROJECTIONS, AND SERVICE AREA CHARACTERISTICS

The purpose of this section is to identify the land use, population projections, and service area characteristics that affect the planning and design of sewer collection and wastewater facility improvements and the potential funding sources for these improvements.

### Sewer Service Areas

No new comments regarding the existing sewer service areas for the Clallam Bay WWTP and Sekiu WWTP.

The Clallam Bay Corrections Center, located in Clallam County, has a separate WWTP that is owned and operated by the Corrections Center. This WWTP serves all flows coming from the Corrections Center, and the WWTP outfall is shared with Sekiu WWTP.

### Natural Environment

No new comments.

### Water System

No new comments.

### Planning Period

The planning period has been updated to extend through 2046.

### Land Use, Zoning, and Population

No new comments.

### Sewer Connections

No new comments.

### Industries in the Sewer Service Area

No new comments.

# 3.0 - REGULATORY REQUIREMENTS

The purpose of this section is to identify the federal, state, and local regulations that affect the planning and design of wastewater facility improvements and the potential funding sources for these improvements. Clallam Bay’s and Sekiu’s existing WWTPs and outfalls are located in Washington State and are therefore regulated by the Department of Ecology.  Collection system projects are not covered in this chapter; however, the permitting required for these projects will likely include local and Clallam County permits and also potentially an Archeological and Cultural Resources Survey depending on the funding source. For alternative reference the Clallam Bay Corrections Center permit information has been included as well.

### Federal Clean Water Act – NPDES

Please reference pages 3-1 to 3-3 in the GP.

The current NPDES Permit for Clallam Bay WWTP (WA002443) was issued on December 1, 2018 and expires November 30, 2023. See Appendix E.

The most recent NPDES Permit for Sekiu (WA0024449) was issued September 4, 2014 and expired September 30, 2019. According to the Washington State Department of Ecology (Ecology), expired permits remain in effect until either the permittee applies for renewal or Ecology requests action on the part of the permittee.

The current NPDES permit for Clallam Bay Corrections Center (WA0039845) expired January, 31, 2022. A permit renewal application has been submitted and received by Ecology, so in accordance with RCW 34.05.422(3) and WAC 173-220-180(5), the current permit and its terms and conditions are administratively extended and will remain in effect and enforceable until a new permit is issued.  See Appendix E.

### Puget Sound Nutrient General Permit

The Department of Ecology has instituted the new Puget Sound Nutrient General Permit (PSNGP) to limit the growth of nutrients discharged into the Puget Sound by wastewater treatment facilities. The PSNGP applies to both the Sekiu and Clallam Bay WWTPs as they are two of the 58 publicly-owned domestic wastewater treatment plants discharging into the Washington Waters of the Salish Sea. The PSNGP also applies to the Clallam Bay Corrections Center. The PSNGP went into effect April 1, 2022, for Clallam Bay WWTP and Sekiu WWTP, and March 1, 2022, for the Clallam Bay Corrections Center.  See Appendix E for permits.

The PSNGP identifies the Clallam Bay WWTP, Sekiu WWTP, and Clallam Bay Corrections Center WWTP under Special Condition S6, Category S, (WWTPs with small loads).

Requirements for both Sekiu and Clallam Bay as identified in the PSNGP, include:

      - Monitoring: Monitor and report per the requirements in PSNGP S7.C. This requirement adds sampling and reporting for Total Ammonia, Nitrate & Nitrite, TKN, and Total Inorganic Nitrogen.

      - Nitrogen Optimization Plan: Submit one Optimization Report per the requirements in PSNGP S6.B. This consists of a developing, implementing, and maintaining a Nitrogen Optimization Plan, including treatment process performance assessment and optimization implementation.  This plan must be submitted by March 31, 2026.

      - AKART Analysis: Submit an AKART Analysis per the requirements in S6.C.  This analysis shall be done in accordance with RCW 90.48 for the purposes of evaluating reasonable treatment alternatives capable of reducing Total Inorganic Nitrogen (TIN).  This report must be submitted by December 31, 2025. Permittees who maintain an annual TIN average of <10 mg/L and do not document an increase in load in their DMRs do not have to submit the AKART Analysis.

### Federal Endangered Species Act

Please refer to page 3-3 in the GP.

### National Environmental Policy Act (NEPA)

Please refer to page 3-4 in the GP.

### State Environmental Review Process (SERP)

Per Washington State Department of Ecology Publication 20-10-024, the Clean Water Act requires Ecology to ensure a complete review of the potential environmental impacts of treatment works projects financed through the State Water Pollution Control Revolving Fund.  Ecology may use the National Environmental Policy Act (NEPA) or they may provide a state equivalent review for approval by the EPA.  This review is referred to as the State Environmental Review Process, or SERP.

The components of environmental review (facility plan, reasonable alternative, SEPA, permitting, mitigation, public outreach) provide the necessary items for Ecology to make a SERP determination.  These components make up what is often referred to as a SERP package.

The SERP package contains elements of environmental and cultural review that Ecology can use to make a complete SERP review of the project. The SERP package requirements were updated in January 2021 and include the following components:

- SEPA Review Documentation including the SEPA checklist and Threshold Determination

- Evidence of public participation opportunities throughout the project

- Documentation of the socioeconomic, Environmental Justice and Civil Rights impacts of the project

- Completed Ecology Executive Order 21-02/Section 106 Cultural Resources Review

- Designated Equivalency Projects Section

- Documentation of other permits, environmental laws or consultations triggered by the project or its funding

The SERP package is submitted to the Ecology project manager and environmental coordinator for review. The SERP deadline depends on the loan type and phase of the project being funded (i.e., planning, design, construction, etc.).  Table 2-1 shows the timing for various loan types and phases.

Table 2-1:  SERP Timing

| Loan Type/Phase | SERP Deadline |
| --- | --- |
| Planning Phase | Include as a deliverable in the funding agreement |
| Design Phase | Include as a deliverable in the funding agreement |
| Design & Construction Phase | Before starting construction |
| Construction Only Phase | Before signing the funding agreement |

### State Environmental Policy Act (SEPA)

Please reference page 3-9 in the GP.

A SEPA has been completed for the GP Amendments and is in Appendix G.

### Investment Grade Efficiency Audit (IGEA)

Per Engrossed Substitute House Bill 1497 Section 1021 projects involving repair, replacement, or improvement of a wastewater treatment plant or other public works facility for which an investment grade audit is obtainable, the public works board must require as a contract condition that the project sponsor undertake an investment grade audit.

There are currently four ways that a project can meet the IGEA requirement:

- Provide documentation that IGEA requirements have been met in the past

  - An audit showing potential energy savings

  - A design review

  - Documentation must be less than 3 years old

- Provide a third-party design review of the project

  - The design review will focus on the energy intensive process: motors, pumps, blowers, etc.

  - A design firm can sub-out to a qualified third party for “peer review” on the energy components

  - The design review can also be conducted by the power provider, if available.

- Demonstrate that the project has no “obtainable” energy savings

  - This only applies to projects receiving funding with no energy use, i.e., “pipes and pavement”

- Complete a preliminary energy audit and/or an IGEA on the existing system

  - An IGEA will identify cost effective energy strategies to save power and money

  - The audit can be prepared by the power provider or an Energy Services Company (ESCO)

### Cost and Effectiveness Analysis (CEA)

Projects receiving funding from the Clean Water State Revolving Fund (CWSRF) must certify that a Cost and Effectiveness Analysis (CEA) has been conducted. A CEA must include a comparison of the life-cycle costs of alternatives, taking into account:

- The cost of constructing the project or activity

- The cost of operating and maintaining the project or activity over the life of the project or activity

- The cost of replacing the project or activity

- The selection, to the maximum extent practicable, of a project or activity that maximizes the potential for efficient water use, reuse, recapture, and conservation, and energy conservations.

The CEA certification is completed in the Ecology Administration of Grants and Loans system (EAGL), and must occur prior to loan signing for activity projects, facility design projects, facility construction projects, and combined facility design/construction projects.  The content of this plan is intended to cover the CEA requirements for the recommended projects.

### Archaeological and Cultural Resources Survey

In April 2021, the Governor of Washington signed Executive Order 21-02 which requires state agencies to review capital construction projects for potential impacts to cultural resources if state funds are being used. This review is to be done in conjunction with the Department of Archaeological and Historic Preservation (DAHP) and any affected Tribes.

If the project receives federal funding, the federal counterpart to Executive Order 21-02, Section 106 of the National Historic Preservation Act will be required instead. On the part of the funding recipient the cultural review process forms are the same and are still submitted to the Ecology project manager and environmental coordinator.

Unless one has been completed recently, an archaeological and cultural resources survey will need be completed during any design phase of WWTP improvements projects where ground disturbance is required (including geotechnical testing). During design, the County will contract with a state approved archaeologist to perform the survey and to consult with the DAHP and affected Tribes. The archaeologist’s report will include survey findings as well as any recommended mitigations such as construction monitoring.

Note that for projects that will be using Department of Ecology funding, the cultural resources must be completed before any ground disturbance, and Department of Ecology will need to perform its own cultural resources review, getting concurrence from DAHP and tribes.

### Stormwater Permitting in the State of Washington

As part of the federal Clean Water Act, the Department of Ecology administers the State of Washington’s Construction Stormwater General Permit. Construction runoff is considered a point source of water pollution and therefore an NPDES permit is required. The State of Washington has developed a General Permit for Construction Stormwater.

Construction stormwater permit coverage is required if the project disturbs more than one-acre of land and the possibility exists of stormwater runoff entering waters of the state or conveyance systems that deliver stormwater to waters of the state.

As such, depending on project size, future WWTP improvements may require coverage under the Construction Stormwater General Permit.  This would entail preparation of a project-specific Stormwater Pollution Prevention Plan (SWPPP), which would be submitted to and reviewed/approved by the County during the design phase.

### Shoreline Permit

Please reference page 3-10 in the GP.

### Hydraulic Project Approval

Please reference page 3-11 in the GP.

### Clallam County Codes

The collection systems and treatment facilities are located within Clallam County’s jurisdiction. It is anticipated that the following permits will be required by the County:

- Building Permit (to include plumbing and electrical)

- Land Disturbance / Critical Areas Permit

- SEPA Checklist

- Right-of-way / Utility Encroachment Permits

- Shoreline Permit (dependent on alternative selection)

- Zoning Conditional Use Permit (dependent upon alternative selection)

- Critical Area Permit (dependent upon alternative selection)

- Cultural Resource Site Assessment

### Regulatory Summary

A summary of the regulatory requirements for improvements to the Sekiu and Clallam Bay WWTPs is presented in Table 2-2.

Table 2-2:  Summary of Regulatory Requirements

| Permit/Report | Agency | Comments/Timeframe |
| --- | --- | --- |
| NPDES Permit | Department of Ecology | The design of future improvements will meet current and anticipated future NPDES requirements. |
| NEPA | Federal – varies depending on project/federal trigger | To be submitted during design phase if project receives federal funding (such as USDA). Environment Assessment to be completed prior to construction. |
| SERP | Department of Ecology (as required by EPA) | Timeframe varies, see Table 2-1. |
| SEPA | County/Ecology | Planning SEPA: To be submitted with this report. Project SEPA: If required by SERP, to be submitted per Table 2-1. |
| IGEA | Department of Ecology | To be completed during design phase. |
| CEA | Department of Ecology | Certification to be completed prior to loan signing with Ecology. |
| Cultural/Archaeological Survey | DAHP/Clallam County | To be completed during design phase. |
| Shoreline Permit | Clallam County | To be submitted during design phase. |
| HPA | WDFW / USAC | Not required for wastewater treatment plant. Will be required for any outfall project. |
| Aquatic Lease | WDNR | May be required for outfall improvements, to be completed during the design phase. |
| Construction Stormwater Permit | Department of Ecology | To be submitted during design phase. |
| Building, Electrical and Plumbing Permits | Clallam County | To be submitted during design phase. |

### Funding

The main funding options for the Sekiu and Clallam Bay projects are listed below. Funding options are often dependent upon the stage of planning and construction the project is in, the financial hardship of the community the WWTPs are serving and the overall demonstrated need of the project. Please reference the funding table in Appendix C.

#### Department of Ecology – CWSRF

The Integrated Water Quality Funding program is the DOE’s application process for funding utilizing the State Revolving Fund (SRF). Loan interest rates depend on the loan term and up to $150,000,000 is available statewide. Communities that qualify for hardship status are eligible for up to $5,000,000 in grants/loan forgiveness (Please see Table 9-7). Applicants can apply for planning, design or construction funding.

The DOE application opens annually in August and applicants hear about funding awards in January of the following year.

Please reference page 9-8 in the GP.

#### USDA – Rural Development – Water and Waste Disposal Loans and Grants

The USDA Rural Development (RD) loans and grants are federal funds distributed by the USDA on an as-available basis. Funds may be used for planning, design and construction and may be back dated. The application is open year-round and the processing time for applications is dependent upon the application.

Please reference page 9-9 in the GP.

#### Department of Commerce – Community Development Block Grant

Per the 2021 General Purpose Grant Overview, the “Community Development Block Grant is a state administered federal grant that funds eligible local governments for community development projects principally benefiting low- and moderate-income persons.” Eligibility for CDBG is dependent on the percentage of low- and moderate-income (LMI) people in the affected community (greater than 51%). According to the 2019 HUD LMI Data Clallam Bay has an LMI of 77.6%, which qualifies it for the CDBG grant funding, but the community of Sekiu does not have a listed LMI. A survey may need to be completed to determine eligibility. Construction awards up to $900,000 are available.

The CDBG application opens annually in the spring and is due in early June. Applicants hear about awards in September of the same year. Funds cannot be back dated for design and applicants are subject to “choice limiting actions” clause, which limits activities such as property acquisition, clearing, grading, site prep, construction contract awarding etc.

Please reference page 9-8 in the GP.

#### Rural Community Assistance Corporation

Rural Community Assistance Corporation (RCAC) helps small communities with loans for smaller capital needs projects, such as surveys or small improvements. Applications are available year-round.

THIS PAGE INTENTIONALLY LEFT BLANK

# 4.0 – EXISTING FACILITIES

The purpose of this section is to describe the existing facilities within the Clallam Bay – Sekiu wastewater collection and treatment systems. These facilities include pressure and gravity sewers, lift stations, wastewater treatment plants, and outfalls.

### Wastewater Collection System

No new comments.

### Wastewater Treatment Plants

In late May 2021 the bearings for one of the two Sekiu RBC units failed.  The County contacted the equipment supplier (Walker Process Equipment) and procured new bearings and moved forward with repairs.  Up until that point in time, the RBC motor and drive assemblies have performed well and planning efforts are to continue focusing on keeping the existing RBC equipment running until the proposed plant upgrade is finalized.

Inland and uphill from the communities of Sekiu and Clallam Bay is the Clallam Bay Corrections Center. The Corrections Center has a WWTP with an average daily flow of 0.116 MGD. The plant consists of a headworks, two lagoons, and chlorine disinfection. After headworks, wastewater flows to an aerated lagoon for BOD removal, and then to an unaerated lagoon for additional polishing and liquids-solids separation. The unaerated lagoon is dredged periodically to remove accumulated solids. Effluent from the unaerated lagoon flows to the chlorine contact basin for disinfection. The plant’s final effluent flows toward Sekiu, paralleling Access Road, to combine with the effluent from the Sekiu Wastewater Treatment Plant and outfall to Clallam Bay.

The Corrections Center is a potential location for a new centralized WWTP to treat the combined sewage from the Clallam Bay, Sekiu, and Corrections Center Wastewater Treatment Plants. Further discussion of this centralized WWTP option can be found in Chapters 7.0 and 10.0.

Combining the wastewater from the Corrections Center with wastewater from Sekiu is another option discussed further in Chapters 7.0 and 10.0.

THIS PAGE INTENTIONALLY LEFT BLANK

# 5.0 - EXISTING AND PROJECTED WASTEWATER FLOWS AND CHARACTERISTICS

This section describes and analyzes the existing and future flows and loadings to the wastewater treatment facility through a 24-year planning period (2046).  Quantifying the existing loading to the WWTPs is necessary to determine the level at which future flows and loadings will be used to size upgrades to the WWTPs that will be required to meet the demands of future growth and regulatory requirements. This section updates the 2018 Plan Chapter 5.

### Existing Wastewater Flows

#### Annual Average

Table 5-1 and Table 5-2 presents the annual average wastewater influent flows for the Clallam Bay WWTP and Sekiu WWTP during the years 2018 through 2022.

Table 5-1:  Clallam Bay WWTP Annual Average Flow

| Year | Flow (MGD) |
| --- | --- |
| 2018 | 0.0291 |
| 2019 | 0.0293 |
| 2020 | 0.0351 |
| 2021 | 0.0378 |
| 2022 | 0.0417 |
| Average = | 0.0346 |

Table 5-2:  Sekiu WWTP Annual Average Flow

| Year | Flow (MGD) |
| --- | --- |
| 2018 | 0.0693 |
| 2019 | 0.0517 |
| 2020 | 0.0689 |
| 2021 | 0.0696 |
| 2022 | 0.0558 |
| Average = | 0.0631 |

#### Monthly Average

Table 5-3 and Table 5-4 presents monthly average flow measured at the WWTPs for the years 2018 through 2022. It also shows wet weather (November – December) and dry weather (June – August) averages for each year.

Table 5-3:  Clallam Bay WWTP Monthly Average Flow

| Month / Year | Flow (MGD) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 2018 | 2019 | 2020 | 2021 | 2022 |
| Jan | NA | 0.0589 | 0.0707 | 0.0660 | 0.0519 |
| Feb | 0.0363 | 0.0321 | 0.0465 | 0.0408 | 0.0291 |
| Mar | 0.0235 | 0.0227 | 0.0255 | 0.0376 | 0.0375 |
| Apr | 0.0314 | 0.0248 | 0.0213 | 0.0225 | 0.0369 |
| May | 0.0197 | 0.0214 | 0.0219 | 0.0194 | 0.0296 |
| Jun | 0.0222 | 0.0221 | 0.0229 | 0.0210 | 0.0266 |
| Jul | 0.0210 | 0.0239 | 0.0227 | 0.0217 | 0.0240 |
| Aug | 0.0199 | 0.0213 | 0.0217 | 0.0198 | 0.0212 |
| Sep | 0.0231 | 0.0247 | 0.0261 | 0.0251 | 0.0222 |
| Oct | 0.0243 | 0.0336 | 0.0283 | 0.0399 | 0.0205 |
| Nov | 0.0398 | 0.0322 | 0.0481 | 0.0787 | 0.0314 |
| Dec | 0.0611 | 0.0355 | 0.0609 | 0.0614 | 0.0673 |
| Annual Average: | 0.0293 | 0.0294 | 0.0347 | 0.0378 | 0.0332 |
| Wet Weather (Nov-Feb) Average | 0.0457 | 0.0397 | 0.0566 | 0.0617 | 0.0449 |
| Dry Weather (June-Sep) Average | 0.0215 | 0.0230 | 0.0233 | 0.0219 | 0.0235 |

Table 5-4:  Sekiu WWTP Monthly Average Flow

| Month/ Year | Flow (MGD) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 2018 | 2019 | 2020 | 2021 | 2022 |
| Jan | 0.1559 | 0.1204 | 0.1800 | 0.1175 | 0.0925 |
| Feb | 0.0669 | 0.0590 | 0.0800 | 0.0815 | 0.0497 |
| Mar | 0.0537 | 0.0334 | 0.0443 | 0.0658 | 0.0668 |
| Apr | 0.0883 | 0.0579 | 0.0350 | 0.0379 | 0.0674 |
| May | 0.0281 | 0.0259 | 0.0365 | 0.0276 | 0.0573 |
| Jun | 0.0230 | 0.0217 | 0.0361 | 0.0270 | 0.0453 |
| Jul | 0.0221 | 0.0289 | 0.0290 | 0.0234 | 0.0324 |
| Aug | 0.0202 | 0.0233 | 0.0270 | 0.0222 | 0.0219 |
| Sep | 0.0421 | 0.0441 | 0.0469 | 0.0460 | 0.0206 |
| Oct | 0.0489 | 0.0798 | 0.0746 | 0.1102 | 0.0201 |
| Nov | 0.1241 | 0.0580 | 0.1099 | 0.1689 | 0.0725 |
| Dec | 0.1487 | 0.0673 | 0.1192 | 0.1088 | 0.1298 |
| Annual Average: | 0.0685 | 0.0516 | 0.0682 | 0.0697 | 0.0564 |
| Wet Weather (Nov-Jan) Average | 0.1239 | 0.0762 | 0.1223 | 0.1192 | 0.0861 |
| Dry Weather (June-Aug) Average | 0.0268 | 0.0295 | 0.0347 | 0.0296 | 0.0300 |

#### Peak Month and Peak Day

Tables 5-5 and 5-6, below, summarize the peak month and peak day flows as recorded at Clallam Bay WWTP and Sekiu WWTP for the years 2018 through 2022.  Peak month and peak day flows for both treatment plants have historically occurred during the winter months, and typically coincide with rain events and inflow and infiltration (I&I) in the collection system.

Table 5-5:  Clallam Bay WWTP Peak Month and Peak Day Flows

| Year | Peak Month Flow (MGD) | Month | Peak Day Flow (MGD) | Month |
| --- | --- | --- | --- | --- |
| 2018 | 0.061 | December | 0.106 | November |
| 2019 | 0.059 | January | 0.156 | January |
| 2020 | 0.071 | January | 0.191 | February |
| 2021 | 0.079 | November | 0.243 | December |
| 2022 | 0.067 | January | 0.213 | December |
| Average = | 0.067 | Average = | 0.182 |  |
| Maximum = | 0.079 | Maximum = | 0.243 |  |
| Percent of Limit (Avg) = | 56% |  |  |  |
| Permit Limit = | 0.12 |  |  |  |

Table 5-6:  Sekiu WWTP Peak Month and Peak Day Flows

| Year | Peak Month Flow (MGD) | Month | Peak Day Flow (MGD) | Month |
| --- | --- | --- | --- | --- |
| 2018 | 0.156 | January | 0.475 | November |
| 2019 | 0.120 | January | 0.539 | January |
| 2020 | 0.180 | December | 0.394 | December |
| 2021 | 0.169 | November | 0.493 | November |
| 2022 | 0.130 | December | 0.496 | December |
| Average = | 0.151 | Average = | 0.480 |  |
| Maximum = | 0.180 | Maximum = | 0.539 |  |
| Percent of Limit (Avg) = | 104% |  |  |  |
| Permit Limit = | 0.145 |  |  |  |

### Existing Wastewater Loadings (BOD5, TSS)

The influent wastewater quality for both plants is characterized below in Tables 5-7 through 5-10 in terms of 5-day Biochemical Oxygen Demand (BOD5) and Total Suspended Solids (TSS). BOD5 and TSS are the primary concern due to their influence on sizing and selection of wastewater treatment facilities.

Table 5-7:  Clallam Bay WWTP Influent BOD5 and TSS Loading

| Year | Average Daily BOD5 (lb/day) | Max Month BOD5 (lb/day) | Average Daily TSS (lb/day) | Max Month TSS (lb/day) |
| --- | --- | --- | --- | --- |
| 2018 | 45.0 | 62.5 | 37.8 | 62.1 |
| 2019 | 53.9 | 69.9 | 43.4 | 60.0 |
| 2020 | 62.9 | 85.0 | 52.0 | 86.2 |
| 2021 | 60.1 | 75.7 | 47.6 | 66.2 |
| 2022 | 57.3 | 68.1 | 46.4 | 67.5 |
| Average = | 55.8 | 72.2 | 45.4 | 68.4 |
| Maximum = | 62.9 | 85.0 | 52.0 | 86.2 |
| Percent of Limit (Avg) = |  | 54% |  | 40% |
| Permit Limit = |  | 135 |  | 171 |

Table 5-8:  Clallam Bay WWTP Influent BOD Loading, Summer and Winter

| Summer = June-Sep Winter = Nov - Feb | Summer BOD5in | Summer BOD5in | Winter BOD5in | Winter BOD5in |
| --- | --- | --- | --- | --- |
|  | (mg/L) | (lb/day) | (mg/L) | (lb/day) |
| Average = | 337.5 | 54.0 | 186.0 | 65.4 |

Table 5-9:  Sekiu WWTP Influent BOD5 and TSS Loading

| Year | Average Daily BOD5 (lb/day) | Max Month BOD5 (lb/day) | Average Daily TSS (lb/day) | Max Month TSS (lb/day) |
| --- | --- | --- | --- | --- |
| 2018 | 33.6 | 63.7 | 28.3 | 58.5 |
| 2019 | 40.8 | 103.4 | 35.1 | 73.3 |
| 2020 | 48.0 | 88.1 | 47.5 | 99.3 |
| 2021 | 49.4 | 87.7 | 43.8 | 75.6 |
| 2022 | 42.3 | 71.3 | 33.4 | 52.9 |
| Average = | 42.8 | 82.8 | 37.6 | 71.9 |
| Maximum = | 49.4 | 103.4 | 47.5 | 99.3 |
| Percent of Limit (Avg) = |  | 61% |  | 42% |
| Permit Limit = |  | 135 |  | 171 |

Table 5-10:  Sekiu WWTP Influent BOD5 Loading, Summer and Winter

| Summer = July-Sep Winter = Nov - Jan | Summer BOD5in | Summer BOD5in | Winter BOD5in | Winter BOD5in |
| --- | --- | --- | --- | --- |
|  | (mg/L) | (lb/day) | (mg/L) | (lb/day) |
| Average = | 348.9 | 66.5 | 46.3 | 28.2 |

Peak month influent BOD5 loading is currently about 72.2 lb/day, or 54% of the permit limit for Clallam Bay, and 82.8 lb/day, or 61% of the permit limit for Sekiu. Figure 5-1 below shows that January historically has high BOD loads and the highest flows at the Clallam Bay WWTP. Figure 5-2 below shows that September historically has high BOD loads entering the Sekiu WWTP and January has high flow.

###### Figure 5-1: Clallam Bay Monthly Average Influent BOD5 (lb/day) 2018-2022

###### Figure 5-2: Sekiu Monthly Average Influent BOD5 (lb/day) 2018-2022

### Existing Nutrient Concentrations

Tables 5-11 and 5-12 below show the results of recent sampling analyzing influent and effluent nutrient levels for Clallam Bay WWTP and Sekiu WWTP. The data suggest that average influent nutrient and CBOD5 concentrations throughout the year for both treatment plants are comparable to typical medium- to high-strength municipal wastewater. The BOD5:TKN ratios were estimated based on a CBOD/BOD conversion factor of 0.83, as is used in WAC 173-221-050. The estimated BOD5:TKN ratios suggest both plants should generally have the capability for denitrification year-round.

Table 5-11: Clallam Bay WWTP Nutrient Concentrations

|  | INFLUENT |  |  |  | EFFLUENT |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sample Date | TKN (mg/L) | AMMONIA (mg/L) | CBOD5 (mg/L) | BOD5:TKN RATIO(1) | TKN (mg/L) | AMMONIA (mg/L) | NOx (mg/L) | TIN (mg/L) |
| 4/26/2022 | 31 | 22 | 87 | 2.8 | 7.01 | 3.82 | 16.9 | 23.91 |
| 4/28/2022 | 31.7 | 21.7 | 220 | 6.9 | 7.07 | 3.63 | 17.1 | 24.17 |
| 5/9/2022 | 37.1 | 32 | 140 | 3.8 | 8.35 | 5.46 | 19.1 | 27.45 |
| 5/17/2022 | 35.3 | 27.8 | 130 | 3.7 | 5.01 | 2.53 | 14.4 | 19.41 |
| 6/9/2022 | 38 | 37.9 | 210 | 5.5 | 1.81 | 0.415 | 12.4 | 14.21 |
| 6/13/2022 | 28 | 28 | 200 | 7.1 | 4.83 | 1.89 | 12.9 | 17.73 |
| 7/13/2022 | 45 | 34.4 | 180 | 4.0 | 34.9 | 1.6 | 17.7 | 51.5 |
| 7/27/2022 | 52.3 | 38.9 | 310 | 5.9 | 3.24 | 0.806 | 16.6 | 16.24 |
| 8/11/2022 | 51.8 | 42.8 | 340 | 6.6 | 2.93 | 1.48 | 13 | 17.83 |
| 8/22/2022 | 89.5 | 65.7 | 380 | 4.2 | 3.35 | 0.833 | 14.9 | 19.55 |
| 9/8/2022 | 57 | 43.5 | 260 | 4.6 | 3.95 | 0.813 | 16.2 | 18.75 |
| 9/27/2022 | 53.4 | 42.4 | 300 | 5.6 | 2.08 | 0.885 | 14.8 | 15.18 |
| 10/12/2022 | 39.6 | 30.5 | 170 | 4.3 | 3.66 | 0.875 | 13.1 | 16.46 |
| 10/17/2022 | 52.3 | 30.5 | 280 | 5.4 | 5.85 | 0.729 | 13.5 | 20.55 |
| 11/2/2022 | 40.5 | 41.5 | 190 | 4.7 | 4.69 | 0.635 | 12.8 | 18.29 |
| 11/9/2022 | 33.4 | 24.5 | 140 | 4.2 | 4.99 | 0.565 | 14.7 | 20.59 |
| 12/15/2022 | 25.4 | 21.1 | 110 | 4.3 | 4.22 | 0.364 | 13.6 | 15.52 |
| 12/27/2022 | 42.4 | 24.3 | 140 | 3.3 | 6.76 | 1.24 | 15.6 | 24.46 |
| AVERAGE | 43.5 | 33.9 | 210.4 | 5.8 | 6.3 | 1.7 | 14.8 | 21.2 |

(1)  BOD5:TKN ratios use measured CBOD5 concentrations with the following conversion to BOD5 as used in WAC 173-221-050: BOD5 = CBOD5 / 0.83.

Table 5-12: Sekiu WWTP Nutrient Concentrations

|  | INFLUENT |  |  |  | EFFLUENT |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sample Date | TKN (mg/L) | AMMONIA (mg/L) | CBOD5 (mg/L) | BOD5:TKN RATIO(1) | TKN (mg/L) | AMMONIA (mg/L) | NOx (mg/L) | TIN (mg/L) |
| 4/26/2022 | 15.6 | 7.2 | 19 | 1.5 | 2.23 | 0.086 | 11.4 | 11.486 |
| 4/28/2022 | 16 | 7.94 | 120 | 9.0 | 2.06 | 0.08 | 9.26 | 9.34 |
| 5/9/2022 | 22.4 | 20.6 | 96 | 5.2 | 4.61 | 1.34 | 13.7 | 15.04 |
| 6/9/2022 | 20 | 20.2 | 110 | 6.6 | 0.872 | 0.394 | 13.3 | 13.694 |
| 6/13/2022 | 30.8 | 32.3 | 140 | 5.5 | 2.9 | 0.885 | 1.91 | 2.795 |
| 7/13/2022 | 49.2 | 40.4 | 170 | 4.2 | 13.2 | 5.28 | 26.7 | 31.98 |
| 7/27/2022 | 53.8 | 40.8 | 320 | 7.2 | 7.96 | 5.77 | 28.8 | 34.57 |
| 8/11/2022 | 41.2 | 36 | 340 | 9.9 | 4.71 | 1.28 | 20.4 | 21.68 |
| 8/22/2022 | 58.3 | 40.3 | 380 | 7.9 | 6.79 | 3.36 | 28.8 | 32.16 |
| 9/8/2022 | 53.2 | 46.8 | 200 | 4.5 | 12.8 | 9.88 | 28.6 | 38.48 |
| 9/27/2022 | 64.4 | 59.2 | 380 | 7.1 | 4.06 | 5.42 | 25 | 30.42 |
| 10/12/2022 | 29.8 | 19.2 | 180 | 7.3 | 2.45 | 1.18 | 22.5 | 23.68 |
| 10/17/2022 | 54.1 | 35.6 | 250 | 5.6 | 4.95 | 0.567 | 22.4 | 22.967 |
| 11/2/2022 | 6.08 | 4.05 | 37 | 7.3 | 3.08 | 0.157 | 4.76 | 4.917 |
| 11/9/2022 | 6.71 | 2.56 | 46 | 8.3 | 2.78 | 0.152 | 4.78 | 4.932 |
| 12/15/2022 | 7.97 | 3.92 | 32 | 4.8 | 1.27 | 0.054 | 5.46 | 5.514 |
| 12/27/2022 | 11.6 | 8 | 29 | 3.0 | 0.729 | 0.108 | 7.78 | 7.888 |
| AVERAGE | 48.3 | 40.0 | 146.1 | 4.6 | 5.1 | 3.2 | 11.2 | 14.4 |

(1)  BOD5:TKN ratios use measured CBOD5 concentrations with the following conversion to BOD5 as used in WAC 173-221-050: BOD5 = CBOD5 / 0.83.

### Clallam Bay Corrections Center Flows and Loadings

Some of the proposed wastewater treatment alternatives discussed in Chapters 7.0 and 10.0 consider combining wastewater flows from Clallam Bay and Sekiu with flows from the Clallam Bay Corrections Center in one centralized treatment plant. For reference, existing flows for the Clallam Bay Corrections Center are listed below in Tables 5-13 and 5-14.

Table 5-13:  Clallam Bay Corrections Center WWTP Annual Average Flow

| Year | Influent Flow (MGD) | Effluent Flow (MGD) |
| --- | --- | --- |
| 2018 | 0.140 | 0.157 |
| 2019 | 0.118 | 0.129 |
| 2020 | 0.116 | 0.140 |
| 2021 | 0.088 | 0.111 |
| 2022 | 0.046 | 0.059 |
| Average = | 0.116 | 0.134 |

Table 5-14:  Clallam Bay Corrections Center WWTP Peak Month and Peak Day Influent Flows

| Year | Peak Month Flow (MGD) | Month | Peak Day Flow (MGD) | Month |
| --- | --- | --- | --- | --- |
| 2018 | 0.160 | January | 0.223 | November |
| 2019 | 0.155 | January | 0.245 | January |
| 2020 | 0.141 | January | 0.183 | January |
| 2021 | 0.124 | February | 0.176 | February |
| 2022 | 0.059 | December | 0.126 | November |
| Average = | 0.128 | Average = | 0.191 |  |
| Maximum = | 0.160 | Maximum = | 0.245 |  |
| Percent of Limit = | 121% |  |  |  |
| Permit Limit = | 0.12 |  |  |  |

Table 5-15:  Clallam Bay Corrections Center WWTP Influent CBOD5 and TSS Loading

| Year | Average Daily CBOD5 (lb/day) | Max Month CBOD5 (lb/day) | Average Daily TSS (lb/day) | Max Month TSS (lb/day) |
| --- | --- | --- | --- | --- |
| 2018 | 170 | 201 | 232 | 258 |
| 2019 | 161 | 206 | 214 | 245 |
| 2020 | 131 | 160 | 204 | 239 |
| 2021 | 123 | 139 | 171 | 226 |
| 2022 | 82.4 | 102 | 84.8 | 112 |
| Average = | 114 | 161 | 181 | 216 |
| Maximum = | 170 | 206 | 232 | 258 |
| Percent of Limit (Avg)= |  | 58% |  | 83% |
| Permit Limit = |  | 278(1) (335 lb/day BOD5) |  | 260 |

(1)  Permitted design criteria includes maximum month BOD5 influent loading of 335 lb/day. Per the facility’s permitted monitoring requirements, CBOD5 is monitored, not BOD5, so the permitted BOD5 influent loading has been converted to CBOD5 using the following conversion, as used in WAC 173-221-050: CBOD5 = CBOD5 * 0.83.

Table 5-16:  Clallam Bay Corrections Center WWTP Influent CBOD5 Loading, Summer and Winter

| Summer = June-Sep Winter = Nov - Feb | Summer CBOD5in | Summer CBOD5in | Winter CBOD5in | Winter CBOD5in |
| --- | --- | --- | --- | --- |
|  | (mg/L) | (lb/day) | (mg/L) | (lb/day) |
| Average = | 193 | 130 | 153 | 135 |

### Future Projected Wastewater Flows

Wastewater average daily flow is projected to increase at a growth rate of 1.0% for both Clallam Bay WWTP and Sekiu WWTP. This growth rate was determined based on historical growth and future anticipated developments within the Clallam Bay and Sekiu urban growth area, as reported in the 2018 Facilities Plan.  Census data from 2020 estimates the Clallam Bay Sekiu UGA population to be 535.  The average population growth rate from 2000 to 2020 is -1.5%.  Table 5-17 below shows the estimated Clallam Bay – Sekiu UGA population projected for 2022 and 2046, based on the 2017 population estimate noted in the 2018 Facilities Plan.

Table 5-17:  Clallam Bay and Sekiu UGA Population Projections

|  | Existing (2022) | Projected (2046) |
| --- | --- | --- |
| UGA Population Estimate(1) | 591 | 750 |

(1) Population calculated using State OFM estimated 2017 population escalated by the 1 percent annual growth rate noted in the 2007 Clallam County Urban Growth Area Analysis and 10-Year Review.

Tables 5-18 and 5-19 below shows the existing and projected average and peak flows to the Clallam Bay WWTP and Sekiu WWTP, respectively.

Table 5-18:  Clallam Bay WWTP Projected Flows

|  | Permit Limit | Existing (2022) | Projected (2046) |
| --- | --- | --- | --- |
| Average Daily Flow (MGD) | -- | 0.033 | 0.042 |
| Peak Month Flow (MGD) | 0.120 | 0.079 | 0.085 |
| Peak Day Flow (MGD) | -- | 0.243 | 0.308 |

Table 5-19:  Sekiu WWTP Projected Flows

|  | Permit Limit | Existing (2022) | Projected (2046) |
| --- | --- | --- | --- |
| Average Daily Flow (MGD) | -- | 0.063 | 0.080 |
| Peak Month Flow (MGD) | 0.145 | 0.180 | 0.192 |
| Peak Day Flow (MGD) | -- | 0.539 | 0.685 |

Average influent flows seen at the Clallam Bay Corrections Center WWTP have been decreasing over at least the past five years, and the Clallam Bay Corrections Center is not expected to grow in the foreseeable future, so future projections for the Corrections Center WWTP have been determined using a conservative growth rate of 0.0%.  The 2022 average daily flow was 0.046 MGD. The existing and projected average and peak flows to the Clallam Bay Corrections Center WWTP are shown below in Table 5-20.

Table 5-20:  Clallam Bay Corrections Center WWTP Projected Flows

|  | Permit Limit | Existing (2022) | Projected (2046) |
| --- | --- | --- | --- |
| Average Daily Flow (MGD) | -- | 0.102 | 0.102 |
| Peak Month Flow (MGD) | 0.120 (influent) | 0.128 | 0.128 |
| Peak Day Flow (MGD) | -- | 0.191 | 0.191 |

### Future Projected Wastewater Loadings (BOD, TSS)

Influent loadings of BOD and TSS are expected to increase proportionally with increase in flow for the Clallam Bay and Sekiu WWTPs. In other words, the concentration will remain the same, while the loading will increase as the flow increases.  Table 5-21 and Table 5-22 show the projected loadings to the Clallam Bay WWTP and the Sekiu WWTP, respectively.

Table 5-21:  Clallam Bay WWTP Projected Loadings

|  | Permit Limit | Existing (2022) | Projected (2046) |
| --- | --- | --- | --- |
| Average BOD5 (lb/day) | -- | 56 | 71 |
| Peak Month BOD5 (lb/day) | 135 | 72 | 92 |
| Average TSS (lb/day) | -- | 45 | 58 |
| Peak Month TSS (lb/day) | 171 | 68 | 87 |

Table 5-22:  Sekiu WWTP Projected Loadings

|  | Permit Limit | Existing (2022) | Projected (2046) |
| --- | --- | --- | --- |
| Average BOD5 (lb/day) | -- | 43 | 54 |
| Peak Month BOD5 (lb/day) | 135 | 83 | 105 |
| Average TSS (lb/day) | -- | 38 | 48 |
| Peak Month TSS (lb/day) | 171 | 72 | 91 |

Figures 5-3 and 5-4 show the existing and projected influent flows and BOD5 loadings up to the year 2046 using on the 1.0% growth rate, for Clallam Bay WWTP and Sekiu WWTP, respectively. Peak month BOD5 loads are below design criteria limits for both Clallam Bay WWTP and Sekiu WWTP, but average flows are above the design criteria for the Sekiu plant showing that improvements to the WWTP should be made as soon as possible.

###### Figure 5-3: Clallam Bay WWTP Existing Peak Month Influent Loading and Flow 2018-2022. 
Projected Peak Month Influent Flow and Loading 2023-2046.

Existing

Projected

###### Figure 5-4: Sekiu WWTP Existing Peak Month Influent Loading and Flow 2018-2022. 
Projected Peak Month Influent Flow and Loading 2023-2046.

Projected

Existing

# 6.0 - COLLECTION SYSTEM EVALUATION

The purpose of this section is to evaluate the existing sewer collection system and existing sewer pumping facilities and their components with respect to capacity, reliability, and redundancy.

The collection system evaluation provided in the October 2018 General Sewer/Wastewater Facilities Plan was reviewed.  Observations with respect to the 2018 evaluation are provided below.

The lift station evaluation provided in the October 2018 General Sewer/Wastewater Facilities Plan was reviewed.  Observations with respect to the 2018 evaluation are provided below.

### I/I Analysis

#### Flow Monitoring

No new comments.

#### Smoke Testing

No new comments.

#### Manhole Inspections

No new comments – repairs not identified in this section. See comments in CCTV Inspection section below.

#### CCTV Inspection

In reviewing the images of the concrete pipes in the October 2018 Plan, it did not appear that the concrete had been degraded sufficiently to warrant the complete replacement of the pipes “due to the age of the system”. Based on staff’s assessment that about 40% of the pipes inspected have separated or misaligned joints, we have assumed that the more cost-effective rehabilitation construction methods such as cure-in-place pipe could be used instead of pipe replacement in approximately half of the sewer mains.

### Hydraulic Model

No new comments.

### Lift Station Capacity Analysis

The 2018 evaluation was not clear as to the source of the lift station capacities. This analysis should be revisited after drawdown tests have been performed to confirm the pumping capacities of each lift station.

### Force Main Capacity Evaluation

This analysis should be revisited after drawdown tests have been performed to confirm the pumping capacities of each lift station.

Additionally, the pumping capacity of the Westend Lift station should be increased to at least 80 gpm in order to achieve the recommended force main flushing velocity of 2.0 feet per second. Likewise, the pumping capacity of the Snob Hill Lift station cannot be decreased from 300 gpm since that flow is required to maintain the recommended force main flushing velocity of 2.0 feet per second.

### Field Observations

No new comments.

### Collection System Improvement Summary

The recommended projects descriptions have been updated to include rehabilitation construction methods where appropriate. Project cost estimates have also been updated to reflect the current scope, and reflect 2023 cost basis. Table 6-12 from the October 2018 General Sewer/Wastewater Facilities Plan has been updated below, and the revised detailed cost analyses for the recommended CIPs is included in Appendix F.

Table 6-12:  Collection System Improvement Projects

| Project No. | Project Name | Project Description | Cost |
| --- | --- | --- | --- |
| CIP 1 | I/I Repair Program | Replace 81 cleanout caps in Sekiu and Clallam Bay; conduct additional CCTV inspection for 3,475 feet in in the Sekiu Airport Road Basin (no change) | $166,100 |
| CIP 2 | Funk & Ballard Pipe Repairs | Repair 6-inch side sewer located north of MH 6.02 in Funk & Ballards, repair one misaligned side sewer connection west of MH 6.02, install a flexible coupling on disjointed PVC pipes downstream of MH 6.02. (no change) | $56,900 |
| CIP 3 | Snob Hill Basin I/I and Pipe Improvements (Phase I) | Replace five sewer manholes (no change). | $147,200 |
| CIP 4 | Area Drain Disconnection | Disconnect area drain in school parking lot from the sanitary sewer; direct to a new infiltration trench west of the parking lot (no change) | $69,000 |
| CIP 5 | Middle Point LS Basin I/I and Pipe Improvements | Replace two side sewers, replace two manholes, install two new manholes and associated 120 LF of new pipe to eliminate a bend between MH 13.05 and MH 13.06 (from CCTV inspection) (no change) | $108,000 |
| CIP 6 | Sekiu LS Basin I/I Improvements | Replace three manholes (from CCTV inspection) (no change) | $98,000 |
| CIP 7 | Clallam Bay I/I Improvements | Replace two manholes (from field inspection) (no change) | $103,700 |
| CIP 8 | Sekiu LS Basin Pipe Improvements | Rehabilitate 3,340 LF of existing concrete pipe with 50% replacement and 50% CIPP; and replace 23 manholes | $1,457,100 |
| CIP 9 | Sekiu LS Airport Pipe Improvements | PROJECT COMPLETED |  |
| CIP 10 | Snob Hill Basin I/I and Pipe Improvements (Phase II) | Rehabilitate 5,845 LF of existing concrete pipe with 50% replacement and 50% CIPP; and replace 13 manholes | $2,633,500 |
| CIP 11 | West End LS Basin Pipe Improvements | Rehabilitate 1,580 LF of existing concrete pipe with 50% replacement and 50% CIPP; and replace 4 manholes | $767,600 |
| CIP 12 | Clallam Bay LS Pipe Improvements | Rehabilitate 13,665 LF of existing concrete pipe with 50% replacement and 50% CIPP; and replace 63 manholes | $6,480,900 |
| CIP 13 | Lighthouse LS Pipe Improvements | Rehabilitate 3,680 LF of existing concrete pipe with 50% replacement and 50% CIPP; and replace 14 manholes | $1,876,300 |
| TOTAL: |  |  | $13,964,300 |

### Lift Station Improvement Summary

The recommended project cost estimates have been updated to reflect our recent experience with lift stations of similar size, and reflect 2023 cost basis. Table 6-13 from the October 2018 General Sewer/Wastewater Facilities Plan has been updated below, and the revised detailed cost analyses for the recommended CIPs is included in Appendix F.

Table 6-13:  Collection System Improvement Projects

| Project No. | Project Name | Project Description | Cost |
| --- | --- | --- | --- |
| CIP 14 | West End LS | New submersible pumps with rail system for removal, new piping and valves in new valve vault, new control and telemetry panels, rehabilitate wet well. | $777,300 |
| CIP 15 | Middle Point LS | New submersible pumps with rail system for removal, new piping and valves in new valve vault, new control and telemetry panels, rehabilitate wet well. | $821,600 |
| CIP 16 | Snob Hill LS | Convert station to submersible type with new submersible pumps with rail system for removal, new piping and valves in new valve vault, new control and telemetry panels. | $821,600 |
| CIP 17.P2 | Sekiu LS-Phase II | New discharge meter in new vault, new control and telemetry panels, connect to existing electrical. | $188,900 |
| CIP 18 | Olson LS | New submersible pumps with rail system for removal, new piping and valves in new valve vault, new control and telemetry panels, rehabilitate wet well. | $732,600 |
| CIP 19 (1) | Clallam Bay LS | Convert station to submersible type with new submersible pumps with rail system for removal, new piping and valves in new valve vault, new control and telemetry panels. | $690,200 |
| CIP 20 (1) | Lighthouse LS | New submersible pumps with rail system for removal, new piping and valves in new valve vault, new control and telemetry panels, rehabilitate wet well. | $878,300 |
| TOTAL: |  |  | $4,910,500 |

(1) Note that the 2018 Facilities Plan switches CIP 19 and CIP 20 in Figure 6-20, Table 6-13, and Figure 8-4. To avoid future confusion, the labels on these figures and table have been fixed and included in Appendix D to show CIP 19 as the Clallam Bay LS, and CIP 20 as the Lighthouse LS.

### WWTP Upgrade-Related Capital Improvement Summary

The various wastewater treatment plant upgrade alternatives presented in Chapter 7.0 may require additional collection system and lift station improvement projects, or revisions to the projects described above. Table 7-11 in Chapter 7.0 summarizes the CIP projects needed for each alternative. Table 6-14 below describes these projects and their associated cost estimates.

Table 6-14:  Capital Improvement Projects Required for WWTP Upgrade Alternatives

| Project No. | Project Name | Project Description | Subtotal Cost (1) | Total Cost |
| --- | --- | --- | --- | --- |
| CIP 15R | Middle Point LS- Revised / Reroute | New removable submersible pumps on rails, new valve vault with new piping and valves, new control panels with telemetry, rehabilitate wet well. Pumps sized to deliver additional flows from Clallam Bay LS to Sekiu WWTP. | $564,432 | $1,035,300 |
| CIP 17R | Sekiu LS – Revised / Reroute | New control panels with telemetry, new larger pumps sized to deliver additional flows from Sekiu WWTP to new HWY 112 LS. | $347,424 | $637,400 |
| CIP 19R | Lighthouse LS – Revised / Reroute | Upgrade pumps and electrical (as needed). Pumps sized to deliver flows to Clallam Bay LS through 4"-inch FM (CIP 38). | $228,492 | $419,200 |
| CIP 20R-A | Clallam Bay LS- Revised / Reroute | Convert station to submersible type with new removable submersible pumps on rails, new valve vault with new piping and valves, new control panels with telemetry. Pumps sized to deliver flows to Middle Point LS. | $433,514 | $795,100 |
| CIP 20R-B | Clallam Bay LS- Revised / Reroute | Convert station to submersible type with new removable submersible pumps on rails, new valve vault with new piping and valves, new control panels with telemetry. Pumps sized to deliver flows to new Eagle Crest #1 LS (CIP 35). | $502,524 | $818,100 |
| CIP 30 | Clallam Bay LS- New Force Main | New 8-inch HDPE force main from Clallam Bay LS to Middle Point LS (approx. 8,400 feet). | $1,995,550 | $3,408,000 |
| CIP 31-A | Sekiu LS- New Force Main to New Lot | New 8-inch HDPE force main from Sekiu LS to HWY 112 WWTP (approx. 2,585 feet). | $354,816 | $600,600 |
| CIP 31-B | Sekiu LS- New Force Main | New 8-inch HDPE force main from Sekiu LS to HWY 112 LS (approx. 1,685 feet). | $253,836 | $429,800 |
| CIP 32 | New HWY 112 LS | New lift station with submersible pumps, telemetry/controls, generator. | $706,992 | $1,296,600 |
| CIP 33 | New Access Rd LS | New lift station with submersible pumps, telemetry/controls, generator. | $682,968 | $1,252,600 |
| CIP 34 | New: Access Rd Force Main | New 12-inch HDPE force main from HWY 112 LS to Access Rd LS, then to the Correction Facility WWTP (approx. 7,725 feet). | $985,809 | $1,668,800 |
| CIP 35 | New: Eagle Crest #1 LS | New lift station with submersible pumps, telemetry/controls, generator. | $669,768 | $1,228,400 |
| CIP 36 | New: Eagle Crest #2 LS | New lift station with submersible pumps, telemetry/controls, generator. | $669,768 | $1,228,400 |
| CIP 37 | New: Eagle Crest Force Main | New 8-inch HDPE force main from Clallam Bay LS to Correction Facility Lagoon (approx. 14,000 feet) | $1,601,463 | $2,710,900 |
| CIP 38 | Lighthouse LS – New Force Main | Install 4-inch HDPE FM to Clallam Bay LS using existing 8-inch gravity sewer as a sleeve. | $225,362 | $381,700 |

(1) Estimated subtotal cost excludes contractor profit, engineering services, sales tax, contingencies, and legal, permitting, and county administration. Cost estimates for WWTP alternatives as shown in Chapter 7.0 use the subtotals listed here. Contractor profit, engineering services, sales tax, contingencies, and legal, permitting, and county administration is included in the overall WWTP alternatives cost estimates (Appendix F).

# 7.0 - Wastewater Treatment Facility Evaluation

The purpose of this section is to evaluate the existing WWTP and its components with respect to performance, capacity, reliability, and redundancy.

A complete facility evaluation was performed in 2022, similar to the evaluation provided in the October 2018 General Sewer/Wastewater Facilities Plan.  Additional findings that were not included in the 2018 evaluation are provided below.

### Historical Plant Performance

#### Clallam Bay WWTP

No new comments.

#### Sekiu WWTP

No new comments.

### Permits

#### Clallam Bay WWTP NPDES Discharge Permits

The Clallam Bay WWTP NPDES permit was finalized, and issued on November 19, 2018.  The permit will expire on November 30, 2023.  This permit contains the same effluent limits as the previous permit.

#### Sekiu WWTP NPDES Discharge Permits

The most recent NPDES Permit for Sekiu (WA0024449) was issued September 4, 2014 and expired September 30, 2019. According to the Washington State Department of Ecology (Ecology), expired permits remain in effect until either the permittee applies for renewal or Ecology requests action on the part of the permittee.

#### Nutrient Removal

The Department of Ecology has instituted the new Puget Sound Nutrient General Permit (PSNGP) to limit the growth of nutrients discharged into the Puget Sound by wastewater treatment facilities. The PSNGP applies to both the Sekiu and Clallam Bay WWTPs as they are two of the 58 publicly-owned domestic wastewater treatment plants discharging into the Washington Waters of the Salish Sea. The PSNGP went into effect April 1, 2022 for Clallam Bay WWTP, April 1, 2022 for Sekiu WWTP and March 1, 2022 for the Clallam Bay Corrections Center.  See Appendix E for permits.

### Facility Evaluation at Projected Design Criteria

#### Influent Screening and Grit Removal

It is noted that maintenance of the settling channels used for grit capture are labor intensive and it would be preferable to consider mechanical grit removal options.

#### Influent Flow Meter

No new comments

#### Primary Clarifiers

Weirs appear to be out of alignment, and corrosion is very noticeable.  Equipment is approaching the end of its useful life.

#### Rotating Biological Contactor Basins (RBC Basin)

In late May 2021 the bearings for one of the two Sekiu RBC units failed.  The County contacted the equipment supplier (Walker Process Equipment) and procured new bearings and moved forward with repairs.  Up until that point in time, the RBC motor and drive assemblies have performed well and planning efforts are to continue focusing on keeping the existing RBC equipment running until the proposed plant upgrade is finalized.

#### Secondary Clarifiers

No new comments

#### Aeration Blowers

No new comments

#### UV Disinfection System

No new comments

#### Aerobic Digesters

No new comments

#### Non-Potable Water System

No new comments

#### Electrical, Control System, and Telemetry

No new comments

#### Outfall

No new comments

### Evaluation of WWTP Alternatives

The purpose of this section is to identify and describe the improvement alternatives to the existing wastewater treatment facilities.  The goal of this evaluation is to select an alternative that is cost effective, reliable and low maintenance, fits within site constraints, and has effective treatment and capacity for current and future flows and loadings. This section updates the WWTP alternatives evaluation discussed in Chapter 7 of the October 2018 General Sewer/Wastewater Facilities Plan.

#### Design Criteria

The Clallam Bay WWTP is not expected to reach permitted max month flow, BOD5 influent or effluent loading, or TSS influent or effluent loading in the 24-year projected time frame. However, the plant components are up to 42 years old and are reaching the end of their useful life.

As described in Chapter 5, the Sekiu WWTP has reported instances of being out of compliance with its NPDES permit limits in the past. In 2014 and 2015, there were exceedances of the permitted maximum month BOD5 influent loading, and there were multiple instances between 2013 and 2022 where the maximum month flow exceeded permit limits.

Permitted influent flows and loadings for each plant, including the Clallam Bay Corrections Center, are listed below in Tables 7-1 through 7-3 for reference.

Table 7-1:  Clallam Current Permitted Influent Flow / Loading Limits

| Current Permitted Facility Load Limits |  |
| --- | --- |
| Maximum Month Design Flow (MMDF) | 0.12 MGD |
| BOD5 Influent Loading for Maximum Month | 135 lb/day |
| TSS Influent Loading for Maximum Month | 171 lb/day |

Table 7-2:  Sekiu Current Permitted Influent Flow / Loading Limits

| Current Permitted Facility Load Limits |  |
| --- | --- |
| Maximum Month Design Flow (MMDF) | 0.145 MGD |
| BOD5 Influent Loading for Maximum Month | 135 lb/day |
| TSS Influent Loading for Maximum Month | 171 lb/day |

Table 7-3:  Corrections Center Current Permitted Influent Flow / Loading Limits

| Current Permitted Facility Load Limits |  |
| --- | --- |
| Maximum Month Design Flow (MMDF) | 0.12 MGD |
| BOD5 Influent Loading for Maximum Month | 335 lb/day |
| TSS Influent Loading for Maximum Month | 260 lb/day |

To address aging infrastructure, permit exceedances, and the need for future nutrient removal, significant upgrades to both wastewater treatment plants are needed.

The tables below identify the design criteria used for sizing and evaluating wastewater facility alternatives.

Table 7-4: Clallam Bay Influent Flows and Loadings

| DESIGN CRITERIA | Existing 2022 | Projected 2046 |
| --- | --- | --- |
| Average Daily Flow | 0.033 | 0.042 |
| Peak Month | 0.079 | 0.085 |
| Peak Day | 0.243 | 0.308 |
| Peak Hour | 0.485 | 0.616 |
| Peak Instantaneous | 0.970 | 1.23 |
| Ave Day BOD5 (lb/day) | 56 | 71 |
| Ave Day TSS (lb/day) | 45 | 58 |
| Peak Month BOD5 (lb/day) | 72 | 92 |
| Peak Month TSS (lb/day) | 68 | 87 |
| Typical Summer ADF | 0.0229 | 0.030 |
| Typical Winter ADF | 0.051 | 0.066 |
| Typical Summer BOD5 (lb/day) | 54 |  |
| Typical Winter BOD5 (lb/day) | 65 |  |
| Typical Inf Water Temperature (Degrees C) | 13.83 |  |
| Average TKN (mg-N/L) | 44 |  |

*Flows Include I/I

Table 7-5: Sekiu Influent Flows and Loadings

| DESIGN CRITERIA | Existing 2022 | Projected 2046 |
| --- | --- | --- |
| Average Daily Flow | 0.063 | 0.080 |
| Peak Month | 0.180 | 0.192 |
| Peak Day | 0.539 | 0.685 |
| Peak Hour | 1.079 | 1.370 |
| Peak Instantaneous | 2.157 | 2.74 |
| Ave Day BOD5 (lb/day) | 43 | 54 |
| Ave Day TSS (lb/day) | 38 | 48 |
| Peak Month BOD5 (lb/day) | 83 | 105 |
| Peak Month TSS (lb/day) | 72 | 91 |
| Typical Summer ADF | 0.0302 | 0.039 |
| Typical Winter ADF | 0.106 | 0.135 |
| Typical Summer BOD5 (lb/day) | 66 |  |
| Typical Winter BOD5 (lb/day) | 28 |  |
| Typical Inf Water Temperature (Degrees C) | 12.96 |  |
| Average TKN (mg-N/L) | 32 |  |

*Flows Include I/I

Table 7-6:  Corrections Center Influent Flows and Loadings

| DESIGN CRITERIA | Existing 2022 | Projected 2047 |
| --- | --- | --- |
| Average Daily Flow | 0.102 | 0.102 |
| Peak Month | 0.128 | 0.128 |
| Peak Day | 0.191 | 0.191 |
| Peak Hour | 0.381 | 0.381 |
| Peak Instantaneous | 0.763 | 0.76 |
| Ave Day BOD5 (lb/day) | 161 | 161 |
| Ave Day TSS (lb/day) | 181 | 181 |
| Peak Month BOD5 (lb/day) | 194 | 194 |
| Peak Month TSS (lb/day) | 216 | 216 |
| Typical Summer ADF | 0.0358 | 0.036 |
| Typical Winter ADF | 0.055 | 0.055 |
| Typical Summer BOD5 (lb/day) | 157 |  |
| Typical Winter BOD5 (lb/day) | 162 |  |
| Average TKN (mg-N/L) | 51 |  |

*Flows Include I/I

Some of the evaluated WWTP upgrade alternatives consider combining wastewater flows from Clallam Bay, Sekiu, and potentially the Clallam Bay Corrections Center. Table 7-7 below lists the design criteria for treatment plant flow options that combine the wastewater flows from Sekiu and the Corrections Center (Flow Option B for Alternatives 2 and 3).

Table 7-7: Sekiu and Corrections Center Combined Influent Flows and Loadings

| DESIGN CRITERIA | Existing 2022 | Projected 2046 |
| --- | --- | --- |
| Average Daily Flow | 0.165 | 0.182 |
| Peak Month | 0.308 | 0.320 |
| Peak Day | 0.730 | 0.875 |
| Peak Hour | 1.460 | 1.751 |
| Peak Instantaneous | 2.920 | 3.50 |
| Ave Day BOD5 (lb/day) | 177 | 188 |
| Ave Day TSS (lb/day) | 219 | 229 |
| Peak Month BOD5 (lb/day) | 244 | 266 |
| Peak Month TSS (lb/day) | 288 | 307 |
| Typical Summer ADF | 0.0660 | 0.074 |
| Typical Winter ADF | 0.160 | 0.190 |
| Average Influent TKN (mg-N/L) | 41 |  |

*Flows Include I/I

Table 7-8 below lists the design criteria for treatment plant flow options that combine the wastewater flows from Sekiu and Clallam Bay (Flow Option C for Alternatives 2 and 3).

Table 7-8: Sekiu and Clallam Bay Combined Influent Flows and Loadings

| DESIGN CRITERIA | Existing 2022 | Projected 2046 |
| --- | --- | --- |
| Average Daily Flow | 0.096 | 0.122 |
| Peak Month | 0.259 | 0.277 |
| Peak Day | 0.782 | 0.993 |
| Peak Hour | 1.564 | 1.986 |
| Peak Instantaneous | 3.128 | 3.97 |
| Ave Day BOD5 (lb/day) | 99 | 125 |
| Ave Day TSS (lb/day) | 83 | 105 |
| Peak Month BOD5 (lb/day) | 155 | 197 |
| Peak Month TSS (lb/day) | 140 | 178 |
| Typical Summer ADF | 0.0531 | 0.068 |
| Typical Winter ADF | 0.156 | 0.201 |
| Average Influent TKN (mg-N/L) | 38 |  |

*Flows Include I/I

Table 7-9 below lists the design criteria for options that combine flow from all three facilities (Alternatives 1 and 4, and Flow Option D for Alternatives 2 and 3).

Table 7-9:  Combined (Sekiu, Clallam Bay and Corrrections Center) Influent Flows and Loadings

| DESIGN CRITERIA | Existing 2022 | Projected 2046 |
| --- | --- | --- |
| Average Daily Flow | 0.198 | 0.223 |
| Peak Month | 0.387 | 0.405 |
| Peak Day | 0.973 | 1.184 |
| Peak Hour | 1.945 | 2.367 |
| Peak Instantaneous | 3.890 | 4.73 |
| Ave Day BOD5 (lb/day) | 260 | 286 |
| Ave Day TSS (lb/day) | 264 | 287 |
| Peak Month BOD5 (lb/day) | 350 | 391 |
| Peak Month TSS (lb/day) | 356 | 394 |
| Typical Summer ADF | 0.0889 | 0.104 |
| Typical Winter ADF | 0.211 | 0.256 |
| Average Influent TKN (mg-N/L) | 41 |  |

*Flows Include I/I

Future Peak Day flows for Clallam Bay and Sekiu were calculated by multiplying Average Daily Flow by the observed peaking factor of existing influent flows. The observed peaking factor of the existing influent flows is 7.38 for Clallam Bay, and 8.55 for Sekiu.

Peak Hour Flow was calculated by multiplying Peak Day Flow by 2.0.  Recorded peak hour flows were not used as the flow metering system has shown to be inaccurate at peak flows.

Peak Instantaneous Design Flow was calculated by multiplying Peak Hour Flow by 2.0.  Recorded peak instantaneous flows were not used as the flow metering system has shown to be inaccurate at peak flows.

Design effluent criteria is listed below in Table 7-10. These criteria were used for all Clallam Bay WWTP and Sekiu WWTP alternative options, as well as all combined treatment plant options. All alternatives consider an effluent Total Inorganic Nitrogen (TIN) limit of 10.0 mg-N/L in anticipation of future nutrient removal requirements.

Table 7-10:  Effluent Design Criteria

| EFFLUENT DESIGN PARAMETER | DESIGN VALUE |
| --- | --- |
| pH | 6-9 |
| Fecal Coliform - Monthly GM | 200/100 |
| Fecal Coliform - 7 Day GM | 400/100 |
| BOD5 (mg/L) Ave. Monthly | 30 |
| TSS (mg/L) Ave. Monthly | 30 |
| BOD5 (mg/L) Ave. Weekly | 45 |
| TSS (mg/L) Ave. Weekly | 45 |
| Total Residual Chlorine Average Monthly | 0.5 mg/L |
| Total Residual Chlorine Average Weekly | 0.75 mg/L |
| Total Ammonia (as N) | 1.0 mg/L |
| Total Inorganic Nitrogen (as N) | 10.0 mg/L |

#### WWTP Alternatives

As part of this amendment to the October 2018 General Sewer/Wastewater Facilities Plan, four new treatment plant alternatives have been evaluated based on Cost Effectiveness (Engineering, Construction and Operations), Treatment Effectiveness, Operations and Maintenance Demands, and Site Layout. The four evaluated alternatives use either Parkson’s Biolac Biological Nutrient Removal System (“Biolac”) or Aeromod’s SEQUOX Biological Nutrient Removal Process (“Aeromod”), and vary in the proposed plant location(s). Two of the alternatives have multiple sub options regarding the flows to be treated at each site. These alternative sub options may combine flows from Sekiu, Clallam Bay, and/or the Corrections Center for treatment.

All evaluated WWTP include the following common elements, similar to the elements described in the 2018 Facilities Plan, page 7-25:

- New or upgraded headworks

- New or upgraded UV disinfection

- Non-potable water system improvements

- Equalization volume

- Instrumentation, telemetry, and controls.

General descriptions of two proposed treatment processes, Biolac and Aeromod, are included below.

##### Biolac Process Description

Parkson’s Biolac Biological Nutrient Removal System is an activated sludge process that uses extended retention of biological solids and cyclical aeration in a single process basin to achieve biological nutrient removal. The treatment process consists of one HDPE-lined earthen basin in which fine bubble membrane diffusers attached to floating aeration chains provide oxygen and mixing. Each chain is controlled individually, which allows for the formation of anoxic and aerated zones within the basin to promote biological nutrient removal.

Influent combines with return activated sludge (RAS) in the anoxic zone at the front end of the basin before it flows into the first stage aeration section of the basin. The sequence of aeration in the first stage aerated and anoxic zones results in a process with sequential nitrification/denitrification reactions.

Downstream of the basin is followed by two integral clarifiers. As with a conventional activated sludge process, flow from the aeration basin enters both clarifiers, where the solids settle to the bottom and clear effluent is collected from the surface and sent to UV disinfection.

Waste activated sludge (WAS) is sent from the clarifiers to the long-term solids digestion basin.

##### Biolac Operations & Maintenance

Operation of the Biolac system is generally straightforward. The aeration is automated, and blowers are automatically turned up or down based on the DO levels in the aeration basins, so the plant will not require constant attention or manual adjustments.

The Biolac activated sludge process is relatively low maintenance. RAS pumping and solids wasting are performed with airlift pumps, which eliminates pump maintenance requirements. The main equipment maintenance requirements are the blowers, flow meters, and electronic actuators. The aeration system will also require occasional cleaning of diffusers, which are accessible without turning off the blowers or draining the tank, so the basin will not require draining to inspect and clean the diffusers. In addition, the clarifiers will require cleaning of the clarifier basin, weirs and launders and require inspection.

##### Biolac Treatment Effectiveness

The effluent from a Biolac system is typically expected to be less than 30 mg/L BOD5, 45 mg/L TSS, and 10 mg-N/L TIN. The Biolac process uses a long hydraulic retention time (HRT) and solids retention time (SRT), which makes the system more forgiving to shock loads and hydraulic surges than conventional activated sludge.

However, the Biolac system is not effective below a minimum flow/loading, and the design flows and loadings originally used for the design of this system, which did not include flow data from 2022, were just at this threshold. After including flow data from the Corrections Center from 2022, it is apparent that projected 2046 flows will be lower than originally expected, and therefore will be too low to work with the Biolac system. The Biolac system will not be an effective treatment option for the projected flows from Clallam Bay, Sekiu, and the Clallam Bay Corrections Center.

##### Aeromod Process Description

The Aeromod SEQUOX process is an activated sludge process that uses cyclical aeration to achieve biological nutrient removal. The treatment process consists of an anoxic selector tank, two stages of aeration basins, two clarifier tanks, and one aerobic digester tank.

Influent combines with return activated sludge (RAS) in the anoxic selector tank before it flows into the first stage aeration basin. Aeration in the first and second stage is turned on and off on a 2-hour cycle for BOD removal and nitrification in aerobic conditions, and denitrification in anoxic conditions. The sequence of aeration in the first stage aeration basin is opposite to that of the second stage, which results in a plug flow process with sequential nitrification/denitrification reactions. Aeration is by coarse bubble diffusers installed on the basin floor.

Similar to a conventional activated sludge process, flow enters the clarifier from the second stage aeration basin, where the solids settle to the bottom and clear effluent is collected from the surface and sent to UV disinfection.

Waste activated sludge (WAS) is sent from the second stage aeration tank to the aerobic digester tank. During the wasting events, supernatant from the digester is decanted back to the aeration basin over a fixed level weir.

##### Aeromod Operations & Maintenance

The Aeromod process is relatively low maintenance. RAS pumping and solids wasting are performed with airlift pumps, and the clarifier has no motors, gears, or electrical components.  The major equipment maintenance requirements are the blowers, flow meters, and electronic actuators. In addition, the diffusers used in the aeration basins and digester are accessible without turning off the blowers or draining the tanks, so the basins will not require draining to inspect and clean the diffusers.

The cyclic aeration is automated, and blowers are automatically turned up or down based on the DO levels in the aeration basins, so the plant will not require constant attention or manual adjustments.

This system will require routine maintenance, inspection, and cleaning of its major components. The clarifiers will require cleaning of the clarifier basin, weirs and launders and require inspection. In addition, the aeration system may require occasional cleaning of the diffusers, which can be raised to the surface without the need to take the basin offline.

##### Aeromod Treatment Effectiveness

The effluent from the Aeromod system is estimated to be less than 10 mg/L BOD5, 15 mg/L TSS, 1 mg-N/L ammonia, and 10 mg-N/L TIN. When configured with chemical addition, the process could achieve even lower effluent TIN concentrations.  The Aeromod process uses a long hydraulic retention time (HRT) and solids retention time (SRT), which makes the system more forgiving to shock loads and hydraulic surges than conventional activated sludge. Considering the variable flows and loadings at Sekiu and Clallam Bay, this process would help maintain effluent quality throughout the entire year.

The Aeromod system has a long list of US installations.  From conversations with operators the system is effective and easy to operate and maintain.

The Aeromod system has an integral sludge digester, which will allow sludge to thicken over time and reduce the frequency of sludge removal from the plant.  It will also allow provide a head start in biosolids handling if biosolids handling options are considered in the future, such as treating biosolids to Class B biosolids or constructing a composting system.

##### Alternatives Overview

The evaluated treatment alternatives are described below:

            - Alternative 1: Biolac at Corrections Center

In Alternative 1, a new Biolac treatment system will be constructed at the Clallam Bay Corrections Center to treat the sewage from the Corrections Center, Clallam Bay, and Sekiu. As discussed above, the Biolac system will not be a feasible option based on updated flow data from 2022. However, information regarding this alternative has been included for informational purposes.

            - Alternative 2: Aeromod at New Lot in Sekiu

In Alternative 2, an Aeromod treatment system will be constructed at a new site in Sekiu. There are four options within Alternative 2 in regards to the flows to be treated at this new site.

              - The new Aeromod system at the new lot in Sekiu will only treat flows from Sekiu. An additional new Aeromod system will be constructed at the existing Clallam Bay WWTP to treat flows from Clallam Bay.

              - The new Aeromod system at the new lot in Sekiu will treat flows from Sekiu and the Clallam Bay Corrections Center. An additional new Aeromod system will be constructed at the existing Clallam Bay WWTP to treat flows from Clallam Bay.

              - The new Aeromod system at the new lot in Sekiu will treat flows from Sekiu and Clallam Bay.

              - The new Aeromod system at the new lot in Sekiu will treat flows from Sekiu, the Clallam Bay Corrections Center, and Clallam Bay.

            - Alternative 3: Aeromod at Sekiu WWTP

In Alternative 3, an Aeromod treatment system will be constructed at the existing Sekiu WWTP. There are four options within Alternative 3 in regards to the flows to be treated at this new site.

              - The new Aeromod system at the existing Sekiu WWTP will treat flows only from Sekiu. An additional new Aeromod system will be constructed at the existing Clallam Bay WWTP to treat flows from Clallam Bay.

              - The new Aeromod system at the existing Sekiu WWTP will treat flows from Sekiu and the Clallam Bay Corrections Center. An additional new Aeromod system will be constructed at the existing Clallam Bay WWTP to treat flows from Clallam Bay.

              - The new Aeromod system at the existing Sekiu WWTP will treat flows from Sekiu and Clallam Bay.

              - The new Aeromod system at the existing Sekiu WWTP will treat flows from Sekiu, the Clallam Bay Corrections Center, and Clallam Bay.

            - Alternative 4: Aeromod at Corrections Center

In Alternative 4, a new Aeromod treatment system will be constructed at the Clallam Bay Corrections Center WWTP to treat the sewage from the Corrections Center, Clallam Bay, and Sekiu.

The treatment alternatives were evaluated to meet the design criteria presented in Tables 7-4 through 7-10. The applicable design criteria depend on the combined or individual plant configurations.

For each alternative, other capital improvement projects may be needed in order to implement the proposed treatment system.  The improvements required for each alternative, which are discussed in more detail in Chapter 6.0, Table 6-14, are shown below in Table 7-11.

Table 7-11:  Capital Improvement Projects Required for WWTP Alternatives

|  |  | Alternative |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CIP # | Description | 1 | 2a | 2b | 2c | 2d | 3a | 3b | 3c | 3d | 4 |
| CIP 15R | Middle Point LS – Revised / Reroute |  |  |  |  |  |  |  |  |  |  |
| CIP 17R | Sekiu LS – Revised / Reroute |  |  |  |  |  |  |  |  |  |  |
| CIP 19R | Lighthouse LS – Revise/Reroute |  |  |  |  |  |  |  |  |  |  |
| CIP 20R-A | Clallam Bay LS – Revised / Reroute |  |  |  |  |  |  |  |  |  |  |
| CIP 20R-B | Clallam Bay LS – Revised / Reroute |  |  |  |  |  |  |  |  |  |  |
| CIP 30 | Clallam Bay LS – New Force Main |  |  |  |  |  |  |  |  |  |  |
| CIP 31-A | Sekiu LS – New Force Main to New Lot WWTP |  |  |  |  |  |  |  |  |  |  |
| CIP 31-B | Sekiu LS – New Force Main to HWY 112 LS |  |  |  |  |  |  |  |  |  |  |
| CIP 32 | New: HWY 112 LS |  |  |  |  |  |  |  |  |  |  |
| CIP 33 | New: Access Rd LS |  |  |  |  |  |  |  |  |  |  |
| CIP 34 | New: Access Rd Force Main |  |  |  |  |  |  |  |  |  |  |
| CIP 35 | New: Eagle Crest #1 LS |  |  |  |  |  |  |  |  |  |  |
| CIP 36 | New: Eagle Crest #2 LS |  |  |  |  |  |  |  |  |  |  |
| CIP 37 | New: Eagle Crest Force Main |  |  |  |  |  |  |  |  |  |  |
| CIP 38 | Lighthouse LS – New Force Main |  |  |  |  |  |  |  |  |  |  |

##### Plant Classification

Each alternative, and all flow options within the alternatives, will have the following classification per WAC 173-230-330 (design flow less than 1 MGD):

              - Alternative 1 – Biolac at Corrections Center = Classification II

              - Alternative 2 – Aeromod at New Lot in Sekiu = Classification II

              - Alternative 3 – Aeromod at Sekiu WWTP = Classification II

              - Alternative 4 – Aeromod at Corrections Center = Classification II

#### Alternative 1 – Biolac at Corrections Center

This alternative converts the Clallam Bay Corrections Center WWTP to a Biolac treatment system which would treat flows from Sekiu, Clallam Bay, and the Clallam Bay Corrections Center. Biolac’s HDPE-lined earthen aeration basin and integral clarifiers would be constructed within the Corrections Center WWTP’s existing first lagoon. The existing second lagoon would be converted into a long-term solids digestion basin.

The Biolac Treatment System was used as the basis of this alternative evaluation; however, other wastewater equipment vendors provide similar systems with this configuration.

As discussed above, with updated flow information from 2022, the Biolac system is no longer a feasible treatment option. The Biolac system requires a minimum volumetric load in order to denitrify effectively.  Initially, the flows from the Corrections Center were high enough to achieve the required volumetric load; however, in recent years the flow has decreased year after year.  Unless the flows from the Correction Center increase, the Biolac system will not be an effective option. Regardless, the evaluation of Alternative 1 has still been included below for informational purposes.

##### Alternative 1 Costs (Construction / Operations & Maintenance)

By combining flows with the Corrections Center, costs for this option would be shared between the County and the Corrections Center. The division of costs was estimated based on the fraction of Corrections Center influent flow to be treated compared to the total design flow of the system. The estimated capital cost for this alternative, including contingency, sales tax, and engineering, was estimated to be $24.5 million ($16.5 million estimated capital cost by the County).

The annual operations and maintenance costs for this alternative would be low relative to the other alternatives. Similar to the capital cost, combining treatment with the Corrections Center would allow the County to share O&M costs with the Corrections Center.  This alternative would be expected to have an annual O&M cost of $306,200 ($206,700 estimated O&M cost by the County).

The estimated net present worth 22-year life cycle cost for this alternative is $30,840,000 ($20,817,000 by the County)

##### Site Layout

See Appendix B for a conceptual layout of this alternative.

#### Alternative 2 – Aeromod at New Lot in Sekiu

This alternative evaluates the SEQUOX activated sludge system offered by Aeromod to be constructed at a new lot in Sekiu.  The Aeromod system is a package system in the configuration of a series of rectangular basins, and was used as the basis of this alternative evaluation, though other wastewater equipment vendors provide similar systems with this configuration.

This alternative has four options in regards to the flows treated at the new site in Sekiu.

              - The new Aeromod system at the new lot in Sekiu will treat flows only from Sekiu. Another new Aeromod system will be constructed at the existing Clallam Bay WWTP to treat flows from Clallam Bay.

              - The new Aeromod system at the new lot in Sekiu will treat flows from Sekiu and the Clallam Bay Corrections Center. Another new Aeromod system will be constructed at the existing Clallam Bay WWTP to treat flows from Clallam Bay.

              - The new Aeromod system at the new lot in Sekiu will treat flows from Sekiu and Clallam Bay.

              - The new Aeromod system at the new lot in Sekiu will treat flows from Sekiu, the Clallam Bay Corrections Center, and Clallam Bay.

##### Alternative 2 Costs (Construction / Operations & Maintenance)

Capital costs, including contingency, sales tax, and engineering, for each option presented for this alternative are summarized below in Table 7-12.  For all flow options within this alternative, land acquisition for the new site is expected to add significant cost to the upgrade. Construction costs for options that include flows from Clallam Bay Corrections Center (Flow Option B and D) will be shared between the County and the Corrections Center.

Operation and maintenance (O&M) costs depend on the flow option. Options that combine flows from Sekiu and Clallam Bay have lower O&M costs than options with separate treatment plants. O&M costs for options that include flows from Clallam Bay Corrections Center (Flow Option B and D) will be shared between the County and the Corrections Center.

Table 7-12:  Alternative 2 Cost Estimates

|  | Estimated Capital Cost | Estimated Annual O&M Cost | Estimated 22-Year Life Cycle Cost |
| --- | --- | --- | --- |
| Flow Option A: Sekiu Flows Only w/ Add’l New Aeromod at Clallam Bay | $42,485,000 | $473,900 | $52,335,000 |
| Flow Option B: Sekiu + Corrections Center Flows w/ Add’l New Aeromod at Clallam Bay | $44,327,000 ($31,745,000 by County)(1) | $490,900 ($343,200 by County)(1) | $54,529,000 ($34,085,000 by County)(1) |
| Flow Option C: Sekiu + Clallam Bay Flows | $33,916,000 | $329,100 | $40,756,000 |
| Flow Option D: Sekiu + Clallam Bay + Corrections Center Flows | $35,656,000 ($24,067,000 by County)(1) | $371,600 ($250,800 by County)(1) | $43,379,000 ($29,281,000 by County)(1) |

(1) Options that include flows from the Clallam Bay Corrections Center estimated that costs for the treatment plant costs will be shared between the County and the Corrections Center based on the fraction of the max month flow coming from the Corrections Center versus the total max month design flow of the Sekiu treatment plant.

##### Alternative 2 Site Layout

The advantages and disadvantages of the site layout for each of the four options presented within this alternative are listed in the table below:

Table 7-13:  Alternative 2 Site Layout Advantages and Disadvantages

|  | Advantages/Disadvantages |
| --- | --- |
| Flow Option A: Sekiu Flows Only w/ Add’l New Aeromod at Clallam Bay | Advantages - New site in Sekiu will remove Sekiu WWTP from tsunami zone - There will be a minimal amount of rerouting of flows required Disadvantages - New site in Sekiu will require land acquisition - Clallam Bay WWTP will remain in a floodplain |
| Flow Option B: Sekiu + Corrections Center Flows w/ Add’l New Aeromod at Clallam Bay | Advantages - Corrections Center will share cost of project - New site in Sekiu will remove Sekiu WWTP from tsunami zone Disadvantages - Will require coordination and negotiation with Corrections Center - New site in Sekiu will require land acquisition - Clallam Bay WWTP will remain in a floodplain |
| Flow Option C: Sekiu + Clallam Bay Flows | Advantages - New site in Sekiu will remove Sekiu WWTP from tsunami zone - Clallam Bay WWTP will no longer be in a floodplain Disadvantages - New site in Sekiu will require land acquisition - Adding Clallam Bay flows to process will require a force main in area of landslide hazard, along HWY 112 |
| Flow Option D: Sekiu + Clallam Bay + Corrections Center Flows | Advantages - Corrections Center will share cost of project - New site in Sekiu will remove Sekiu WWTP from tsunami zone - Clallam Bay WWTP will no longer be in a floodplain Disadvantages - Will require coordination and negotiation with Corrections Center - New site in Sekiu will require land acquisition - Adding Clallam Bay flows to process will require a force main in area of landslide hazard, along HWY 112 |

See Appendix B for a conceptual layout of this alternative and all flow options presented here.

#### Alternative 3 – Aeromod at Existing Sekiu WWTP

Alternative 3 evaluates the Aeromod SEQUOX activated sludge system to be constructed at the existing Sekiu WWTP. Similar to Alternative 2, the Aeromod system was used as the basis of this alternative evaluation, but other wastewater equipment vendors provide similar systems with this configuration.

Alternative 3 has four options in regards to the flows treated by the new Aeromod at the existing Sekiu WWTP.

              - The new Aeromod system at the existing Sekiu WWTP will treat flows only from Sekiu. Another new Aeromod system will be constructed at the existing Clallam Bay WWTP to treat flows from Clallam Bay.

              - The new Aeromod system at the existing Sekiu WWTP will treat flows from Sekiu and the Clallam Bay Corrections Center. Another new Aeromod system will be constructed at the existing Clallam Bay WWTP to treat flows from Clallam Bay.

              - The new Aeromod system at the existing Sekiu WWTP will treat flows from Sekiu and Clallam Bay.

              - The new Aeromod system at the existing Sekiu WWTP will treat flows from Sekiu, the Clallam Bay Corrections Center, and Clallam Bay.

##### Alternative 3 Costs (Construction / Operations & Maintenance)

Capital costs, including contingency, sales tax, and engineering, for each option presented for this alternative are summarized below in Table 7-14.  By using the site of Sekiu’s existing WWTP, Alternative 3 has no costs associated with land acquisition, making the capital cost lower than the corresponding flow option presented for Alternative 2. Construction costs for options that include flows from Clallam Bay Corrections Center (Flow Option B and D) will be shared between the County and the Corrections Center.

Operation and maintenance (O&M) costs depend on the flow option. Options that combine flows from Sekiu and Clallam Bay have lower O&M costs than options with separate treatment plants. O&M costs for options that include flows from Clallam Bay Corrections Center (Flow Option B and D) will be shared between the County and the Corrections Center.

Table 7-14:  Alternative 3 Cost Estimates

|  | Estimated Capital Cost | Estimated Annual O&M Cost | Estimated 22-Year Life Cycle Cost |
| --- | --- | --- | --- |
| Flow Option A: Sekiu Flows Only w/ Add’l New Aeromod at Clallam Bay | $29,769,000 | $473,900 | $39,618,000 |
| Flow Option B: Sekiu + Corrections Center Flows w/ Add’l New Aeromod at Clallam Bay | $31,436,000 ($24,268,000 by County)(1) | $490,900 ($343,200 by County)(1) | $41,639,000 ($28,671,000 by County)(1) |
| Flow Option C: Sekiu + Clallam Bay Flows | $23,997,000 | $329,100 | $29,837,000 |
| Flow Option D: Sekiu + Clallam Bay + Corrections Center Flows | $24,563,000 ($16,717,000 by County)(1) | $371,600 ($250,800 by County)(1) | $32,286,000 ($21,793,000 by County)(1) |

(1) Options that include flows from the Clallam Bay Corrections Center estimated that costs for the treatment plant costs will be shared between the County and the Corrections Center based on the fraction of the max month flow coming from the Corrections Center versus the total max month design flow of the Sekiu treatment plant.

##### Alternative 3 Site Layout

The advantages and disadvantages of the site layout for each of the four flow options presented within this alternative are listed in the table below:

Table 7-15:  Alternative 3 Site Layout Advantages and Disadvantages

|  | Advantages/Disadvantages |
| --- | --- |
| Flow Option A: Sekiu Flows Only w/ Add’l New Aeromod at Clallam Bay | Advantages - Using existing sites will not require land acquisition - There will be no need to reroute flows from the existing plants Disadvantages - Sekiu WWTP will remain in a tsunami hazard zone - Clallam Bay WWTP will remain in a floodplain |
| Flow Option B: Sekiu + Corrections Center Flows w/ Add’l New Aeromod at Clallam Bay | Advantages - Existing sites will not require land acquisition - Corrections Center will share cost for project Disadvantages - Will require coordination and negotiation with Corrections Center - Sekiu WWTP will remain in a tsunami hazard zone - Clallam Bay WWTP will remain in a floodplain |
| Flow Option C: Sekiu + Clallam Bay Flows | Advantages - Using existing sites will not require land acquisition - Clallam Bay WWTP will no longer be in a floodplain Disadvantages - Sekiu WWTP will remain in a tsunami hazard zone - Adding Clallam Bay flows to process will require a force main in area of landslide hazard, along HWY 112 |
| Flow Option D: Sekiu + Clallam Bay + Corrections Center Flows | Advantages - Using existing sites will not require land acquisition - Corrections Center will share cost for project - Clallam Bay WWTP will no longer be in a floodplain Disadvantages - Will require coordination and negotiation with Corrections Center - Sekiu WWTP will remain in a tsunami hazard zone - Adding Clallam Bay flows to process will require a force main in area of landslide hazard, along HWY 112 |

See Appendix B for a conceptual layout of this alternative and all flow options presented here.

#### Alternative 4 – Aeromod at Corrections Center

This alternative converts the Clallam Bay Corrections Center WWTP to an Aeromod treatment system which will treat flows from Sekiu, Clallam Bay, and the Clallam Bay Corrections Center. As with Alternatives 2 and 3, the Aeromod system was used as the basis of this alternative evaluation, but other wastewater equipment vendors provide similar systems with this configuration. Sekiu flows will be pumped up the Access Rd force main, and Clallam Bay flows will be pumped up the Eagle Crest force main.

##### Alternative 4 Costs (Construction / Operations & Maintenance)

The estimated costs for this option, including contingency, sales tax, and engineering, were determined to be approximately $37.8 million ($25.5 million estimated capital cost by the County).  The major costs for this alternative are the new force mains, lift stations, excavation, backfill, concrete, and installation of the Aeromod system.

Combining flows from Sekiu, Clallam Bay, and the Corrections Center helps reduce overall maintenance requirements. In addition, combining treatment with the Corrections Center allows the County to share O&M costs with the Corrections Center.  This alternative is be expected to have an annual O&M cost of $371,600 ($250,800 estimated O&M cost by the County).

The estimated net present worth 22-year life cycle cost for the County for this alternative is $45,568,000 ($30,759,000 by the County).

##### Alternative 4 Site Layout

This alternative has the advantages of removing the Sekiu WWTP from the tsunami hazard zone and removing the Clallam Bay WWTP from the floodplain. Also, by combining flows from all three facilities, the Corrections Center would share costs with the County for the project, though coordination and negotiation with the Corrections Center would be needed.

Locating the treatment plant at the Corrections Center would have the significant added cost of multiple new lift stations, force mains, and various revisions to existing lift stations to reroute flows from Sekiu and Clallam Bay to the Corrections Center WWTP.

See Appendix B for a conceptual layout of this alternative.

### Summary of Alternatives

Table 7-16 provides an overall summary of the four presented alternatives and all associated flow options. This table also lists the

Table 7-16:  WWTP Alternatives Summary

| Alt. | Type of Plant | Description | Include Corrections Center? | No. of Plants | Notes |
| --- | --- | --- | --- | --- | --- |
| 1 | Biolac | Sekiu, Clallam Bay, & Corrections all treated at Corrections | Yes | 1 | • No longer feasible |
| 2a | Aeromod (Flow Option A) | Build Aeromod on new lot in Sekiu for just Sekiu flows AND build Aeromod in Clallam Bay for just Clallam Bay flows. | No | 2 | • Clallam Bay would stay in floodplain • Requires land acquisition |
| 2b | Aeromod (Flow Option B) | Build Aeromod on new lot in Sekiu for Sekiu & Corrections flows AND build Aeromod in Clallam Bay for just Clallam Bay flows. | Yes | 2 | • Clallam Bay would stay in floodplain • Requires negotiation and cooperation with Corrections • Requires land acquisition + Corrections helps pay for project |
| 2c | Aeromod (Flow Option C) | Build Aeromod on new lot in Sekiu for Sekiu & Clallam Bay flows. | No | 1 | • Requires forcemain in slide area • Requires land acquisition |
| 2d | Aeromod (Flow Option D) | Build Aeromod on new lot in Sekiu for Sekiu, Clallam Bay, and Corrections flows. | Yes | 1 | • Requires land acquisition • Requires forcemain in slide area • Requires negotiation and cooperation with Corrections + Corrections helps pay for project |
| 3a | Aeromod (Flow Option A) | Build Aeromod at existing Sekiu site for just Sekiu flows AND build Aeromod at Clallam Bay for just Clallam Bay flows. | No | 2 | • Sekiu stays in Tsunami zone • Clallam Bay would stay in floodplain |
| 3b | Aeromod (Flow Option B) | Build Aeromod at existing Sekiu site for Sekiu & Corrections flows AND build Aeromod at Clallam Bay for just Clallam Bay flows. | Yes | 2 | • Sekiu stays in Tsunami zone • Clallam Bay would stay in floodplain • Requires negotiation and cooperation with Corrections + Corrections helps pay for project |
| 3c | Aeromod (Flow Option C) | Build Aeromod at existing Sekiu site for Sekiu & Clallam Bay flows. | No | 1 | • Sekiu stays in Tsunami zone • Requires forcemain in slide area |
| 3d | Aeromod (Flow Option D) | Build Aeromod at existing Sekiu site for Sekiu, Clallam Bay, and Corrections flows. | Yes | 1 | • Sekiu stays in Tsunami zone • Requires forcemain in slide area • Requires negotiation and cooperation with Corrections + Corrections helps pay for project |
| 4 | Aeromod (Flow Option D) | Build Aeromod at Corrections for all three plants | Yes | 1 | • Requires negotiation and cooperation with Corrections + Corrections helps pay for project |

#### Treatment Alternative Cost Estimates

The treatment alternatives discussed in above have been evaluated and a cost estimate has been established for each, presented below in Table 7-17. The construction cost considered in this evaluation is the expected cost to be borne by the County after accounting for the anticipated sharing of costs between the Corrections Center. As noted above, Alternative 1 is no longer a feasible treatment process after accounting for flow data from 2022; cost information for this alternative has been included for informational purposes only.

The estimated construction costs suggest that Alternative A – Flow Options A, B, and C, and Alternative 3 – Flow Option A may be prohibitively expensive. Excluding Alternative 1, the lowest capital cost alternative is Alternative and 3d. Detailed construction cost estimates for all the treatment alternatives are presented in Appendix C.

Table 7-17:  Total Project Construction Cost Estimates for Alternatives

| Process Alternatives | Total Construction Cost Estimate | Estimate of Construction Cost by County (1) |
| --- | --- | --- |
| Alternative 1: Biolac at Corrections Facility | $24,563,000 | $16,580,000 (1) |
| Alternative 2a: Aeromod at New Lot in Sekiu: Sekiu Flows Only w/ Add’l New Aeromod at Clallam Bay | $42,485,000 | $42,485,000 |
| Alternative 2b: Aeromod at New Lot in Sekiu: Sekiu + Corrections Center Flows w/ Add’l New Aeromod at Clallam Bay | $44,327,000 | $31,745,000 (1) |
| Alternative 2c: Aeromod at New Lot in Sekiu: Sekiu + Clallam Bay Flows | $33,916,000 | $33,916,000 |
| Alternative 2d: Aeromod at New Lot in Sekiu: Sekiu + Clallam Bay + Corrections Center Flows | $35,656,000 | $24,067,000 (1) |
| Alternative 3a: Aeromod at Existing Sekiu WWTP: Sekiu Flows Only w/ Add’l New Aeromod at Clallam Bay | $29,769,000 | $29,769,000 |
| Alternative 3b: Aeromod at Existing Sekiu WWTP: Sekiu + Corrections Center Flows w/ Add’l New Aeromod at Clallam Bay | $31,436,000 | $24,268,000 (1) |
| Alternative 3c: Aeromod at Existing Sekiu WWTP: Sekiu + Clallam Bay Flows | $23,997,000 | $23,997,000 |
| Alternative 3d: Aeromod at Existing Sekiu WWTP: Sekiu + Clallam Bay + Corrections Center Flows | $24,563,000 | $16,717,000(1) |
| Alternative 4: Aeromod at Corrections Facility | $37,845,000 | $25,545,000 (1) |

(1) Options that include flows from the Clallam Bay Corrections Center assume costs for the treatment plant costs will be shared between the County and the Corrections Center based on the fraction of the max month flow coming from the Corrections Center versus the total max month design flow of the Sekiu treatment plant. Actual distribution of costs will require coordination with Corrections Center.

As shown below in Table 7-18, with the estimated annual O&M costs, Alternative A – Flow Options A, B, and C, and Alternative 3 – Flow Option A maintain significantly higher 22-year life cycle costs. Excluding Alternative 1, Alternative 3d – Aeromod at the existing Sekiu WWTP to treat flows from Sekiu, Clallam Bay, and the Corrections Center, has the lowest total capital cost, annual O&M cost, and 22-year life cycle cost, after accounting for cost-sharing with the Corrections Center. Detailed O&M cost estimates for all the treatment alternatives are presented in Appendix C. The 22-year life cycle cost estimates for all alternatives were calculated based on the estimated capital and O&M costs, and assume a discount rate of 0.5% and a useful life of 22 years.

Table 7-18:  Overall 22-Year Life Cycle Cost Estimates for Alternatives

|  | Estimated Capital Cost | Estimated Annual O&M Cost | Estimated 22-Year Life Cycle Cost | Estimated 22-Year Life Cycle Cost by County(1) |
| --- | --- | --- | --- | --- |
| Alternative 1: Biolac at Corrections Facility | $24,521,000 ($24,476,000 by County)(1) | $306,200 ($206,685 by County)(1) | $30,840,000 | $20,817,000 (1) |
| Alternative 2a: Aeromod at New Lot in Sekiu: Sekiu Flows Only w/ Add’l New Aeromod at Clallam Bay | $42,485,000 | $473,900 | $52,335,000 | $52,335,000 |
| Alternative 2b: Aeromod at New Lot in Sekiu: Sekiu + Corrections Center Flows w/ Add’l New Aeromod at Clallam Bay | $44,327,000 ($31,745,000 by County)(1) | $490,900 ($343,200 by County)(1) | $54,529,000 | $34,085,000 (1) |
| Alternative 2c: Aeromod at New Lot in Sekiu: Sekiu + Clallam Bay Flows | $33,916,000 | $329,100 | $40,756,000 | $40,756,000 |
| Alternative 2d: Aeromod at New Lot in Sekiu: Sekiu + Clallam Bay + Corrections Center Flows | $35,656,000 ($24,067,000 by County)(1) | $371,600 ($250,800 by County)(1) | $43,379,000 | $29,281,000 (1) |
| Alternative 3a: Aeromod at Existing Sekiu WWTP: Sekiu Flows Only w/ Add’l New Aeromod at Clallam Bay | $29,769,000 | $473,900 | $39,618,000 | $39,618,000 |
| Alternative 3b: Aeromod at Existing Sekiu WWTP: Sekiu + Corrections Center Flows w/ Add’l New Aeromod at Clallam Bay | $31,436,000 ($24,268,000 by County)(1) | $490,900 ($343,200 by County)(1) | $41,639,000 | $28,671,000 (1) |
| Alternative 3c: Aeromod at Existing Sekiu WWTP: Sekiu + Clallam Bay Flows | $23,997,000 | $329,100 | $29,837,000 | $29,837,000 |
| Alternative 3d: Aeromod at Existing Sekiu WWTP: Sekiu + Clallam Bay + Corrections Center Flows | $24,563,000 ($16,717,000 by County)(1) | $371,600 ($250,800 by County)(1) | $32,286,000 | $21,793,000 (1) |
| Alternative 4: Aeromod at Corrections Facility | $37,845,000 ($25,545,000 by County)(1) | $371,600 ($250,830 by County)(1) | $45,568,000 | $30,759,000 (1) |

(1) Options that include flows from the Clallam Bay Corrections Center assume costs for the treatment plant costs will be shared between the County and the Corrections Center based on the fraction of the max month flow coming from the Corrections Center versus the total max month design flow of the Sekiu treatment plant. Actual distribution of costs will require coordination with Corrections Center.

# 8.0 - CAPITAL IMPROVEMENT PROGRAM

The purpose of this section is to evaluate, identify and describe the recommended improvements to the existing sewer collection and wastewater treatment facilities.  Improvements of this section will consist of site improvements and selection of the recommended treatment alternative.  The goal of alternative evaluation is to select an alternative that is cost-effective, reliable, low maintenance, fits within site constraints, and has effective treatment and capacity for current and future flows and loadings.

The County has developed 6-year and 20-year capital improvement plans (CIP), which are included in Appendix D. The CIP includes the anticipated project schedule and estimated project costs based on the recommended treatment alternative. It should be noted that the Capital Improvement Plan in years 2029 – 2042 is planning level, is based on the best information available at this time, and may not include all future sewer capital projects. The CIP will continue to be financed and updated as more information becomes available. It is recommended to review and update the CIP annually.

### Sewer System Capital Improvements

The recommended projects’ descriptions have been updated to include rehabilitation construction methods where appropriate. Project cost estimates have also been updated to reflect the current scope, and reflect 2023 cost basis. The revised scopes and costs are included in the updated Table 6-12 and the revised detailed cost analyses for the recommended CIPs is included in Appendix F.

### Lift Station Capital Improvements

The recommended projects’ descriptions have been updated to include rehabilitation construction methods where appropriate. Project cost estimates have also been updated to reflect the current scope, and reflect 2023 cost basis. The revised scopes and costs are included in the updated Table 6-13 and the revised detailed cost analyses for the recommended CIPs is included in Appendix F.

### Wastewater Treatment Plant Capital Improvements

#### WWTP Recommended Alternative

##### Description of Recommended System

Based on the evaluation of the treatment process alternatives, Alternative 3d, installing an Aeromod system at the existing Sekiu WWTP to treat flows from Sekiu, Clallam Bay, and the Clallam Bay Corrections Center, is recommended as the best alternative for Clallam County, provided that the County and the Corrections Center are open to combining flows and sharing costs.

Alternative 3d has the benefits of removing the Clallam Bay WWTP from the floodplain, reducing O&M costs by providing a centralized treatment plant, and reducing capital and O&M costs for the County by sharing costs with the Corrections Center. Out of all evaluated feasible alternatives, Alternative 3d is expected to have the lowest capital and O&M costs after taking into consideration cost sharing between the Corrections Center and the County.

The process is fundamentally an extended-aeration activated sludge process and thus is effective at treating variable flow and waste loads. The process contains typical characteristics of extended-aeration systems, including long hydraulic and solids retention times, high microorganism concentration, and low food:microorganism ratio (F/M). Primary clarification is unnecessary and would not be utilized. The treatment process consists of an anoxic selector tank, two stages of aeration basins, two clarifier tanks, and one aerobic digester tank, and can achieve denitrification by biological means to meet the anticipated future effluent limits.

A flow schematic for the recommended alternative is included in Appendix A.

##### Future Expansion

The recommended system has been sized and will be designed to satisfy the design criteria presented in Chapter 7.0 in Tables 7-9 and 7-10, which are based on projected 2046 flows. If future expansion becomes necessary, it may be possible to construct additional basins within the existing Sekiu WWTP.

##### Redundancy

The recommended treatment plant improvements will meet all reliability and redundancy requirements for a Class II WWTP as defined by Ecology in the DOE Orange Book Table G2-9.  The proposed treatment system will provide two parallel trains of aeration processes.

##### Preliminary Schedule

Permitting					August 2023 – February 2025

Funding - Apply for Grants / Loans: 		October 2023

Notification of Funding Received:		June 2024

Design Phase:  					June 2024 – June 2025

Ecology Review: 				June 2025 – July 2025

Bid Phase: 					July 2025 – August 2025

Construction Phase: 				August 2025 – January 2027 (18 months)

#### Future Nutrient Effluent Limits

It is our understanding that a future Total Inorganic Nitrogen (TIN) effluent limit may be required for all plants discharging to the Salish Sea.  At this time, the Department of Ecology has not provided a future numeric effluent limit for the anticipated Total Inorganic Nitrogen parameter or a timeline for when this limit may go into effect.

The evaluated treatment alternatives all include the capability of denitrification. With the recommended Aeromod treatment process, a TIN effluent level below 10 mg-N/L will be achievable. If a final numeric TIN effluent limit is determined to be below 10 mg-N/L, the County intends to reevaluate and amend this report at that time if it determined to be necessary.

#### Outfall Improvements

No new comments.

#### Staffing and Testing Requirements

Based on the treatment plant classification listed in Chapter 7.0, the recommended WWTP must have at least a Group II operator in reasonable charge of daily operation. After improvements have been made, it is expected that the WWTP will be operable by two full time employees. The County currently employs two Group III operators for the Sekiu and Clallam Bay WWTPs, so the County’s current staffing will likely be sufficient for the recommended WWTP upgrade.

#### Biosolids Handling

An aerobic digester is included as part of the recommended Aeromod system.  The biosolids will continue to be hauled to the Port Angeles WWTP.  It is anticipated that the solids from the recommended WWTP would be removed from the digester roughly twice a week in a 6,000-gallon septic truck, and it is expected that biosolids hauling costs would be shared between the County and the Corrections Center.  Historical costs and estimated future costs at the projected 2046 average day flow for biosolids removal from the digester are estimated in Table 8-1 below.

Table 8-1:  Biosolids Handling Costs

|  | Clallam County (Sekiu and Clallam Bay) 2020 Biosolids Costs | Clallam County (Sekiu and Clallam Bay) 2021 Biosolids Costs | Sekiu, Clallam Bay, and Corrections Center Biosolids at Future 2046 Average Day Flow |
| --- | --- | --- | --- |
| Estimated Volume Wasted from Digester | 279 GPD | 312 GPD | 1550 GPD |
| Hauling & Tipping Fees | $1,435/trip (6,000 gallons/trip) | $1,435/trip (6,000 gallons/trip) | $1,435/trip (1) (6,000 gallons/trip) |
| Total Annual Costs | $24,395 | $27,265 | $135,309 ($91,333 by County) |

(1) Costs are in 2023 dollars.

#### Construction Phasing

Phasing of construction will be necessary to ensure proper treatment through the existing Sekiu WWTP during construction.  Permit condition S5.C will be met as required. A proposed phasing schedule is outlined below.

- Upgrade the existing headworks.

  - Temporary manual bypass screens can be used to provide screening for the Sekiu WWTP during new headworks installation.

- Construct the recommended Aeromod system upgrades (including SCADA programming and the majority of process piping).

  - Continue existing plant operations at Sekiu, Clallam Bay, and the Corrections Center during construction.

- Install all necessary lift stations and force mains to send Clallam Bay and Corrections Center flows to the existing Sekiu WWTP.

  - Once Aeromod system, new lift stations, and new force mains have been tested, tie-ins can be completed to start operation of the new Aeromod system with flow from Sekiu, Clallam Bay, and Corrections Center.

  - Temporary piping will connect the new headworks to the new Aeromod system until existing basins are converted to equalization.

- Convert the existing RBC and digester basins to an equalization basin.

  - Once completed and tested, the Equalization Basin can be tied in to the treatment plant.

- Existing UV disinfection system can be upgraded.

  - Equalization Basin can help alleviate the need for temporary facilities during the switchover from the old UV system to the new system.

Remaining improvements are not process sensitive and can happen on a typical construction schedule.

#### WWTP Upgrade Costs

Table 8-2 below provides a summary of the estimated construction and O&M costs for the recommended WWTP Alternative 3d, including the portion of cost to be borne by the County.

Table 8-2:  Cost Summary for Recommended WWTP Upgrade

| Estimated Capital Cost | Estimated Annual O&M Cost | Estimated 22-Year Life Cycle Cost | Estimated 22-Year Life Cycle Cost by County(1) |
| --- | --- | --- | --- |
| $24,563,000 ($16,717,000 by County)(1) | $371,600 ($250,800 by County)(1) | $32,286,000 | $21,793,000 (1) |

(1) Estimated costs by the County have been assumed to be shared between the County and the Corrections Center based on the fraction of the max month flow coming from the Corrections Center versus the total max month design flow of the Sekiu treatment plant.

### Capital Improvements Plan Schedule

The 6 and 20-year Capital Improvements Plan Schedules have been updated and are included in Appendix D.

# 9.0 - FINANCIAL ANALYSIS

### Introduction

This financial analysis includes a spreadsheet analysis of the sewer budget over the coming years but focusing primarily on the 6-year CIP costs. The primary objective of this analysis is to provide a basic evaluation of the financial capacity of the sewer utility and spreadsheet tools for investigating CIP and funding options going forward.

### Financial Status of Existing Clallam Bay – Sekiu Wastewater Treatment Plant

Revenues

Existing revenues are insufficient to maintain, operate and improve the sewer system. The County supplements rate payer fees with funds (about $200,000 per year), provided from the General Fund and from REET, in order to cover all operating expenses.

### Connection Fee Calculation Estimate

The sewer system replacement value is a minimum of $40 million based on the CIP alone. Using this low value and an estimated 658 total connections (ERU) for 2040, the value per ERU is a minimum of $62,000. Therefore, the Connection Fee (or General Facility Charge) should be increased from $1500 to a much higher fee. A fee in the range of $5,000 to $10,000 would be comparable to other many other sewer systems.

### Projected Expenses, Revenues, and Capital Reserves

Expenses

Operating expenses are expected to increase at the pace of inflation or faster. The major added expense over the next 20-30 years will be funding the Capital Improvement Program (CIP).

Revenues

Revenues need to be increased:

- Increase Sewer Rates for all customers.

- Increase number of paying customers.

- Increase Connection Fees for all customers.

- Ensure new developments pay appropriate Impact Fee.

Capital reserves

The county currently provides funds to cover operating expense shortfalls. Funding the CIP is the higher priority over establishing a capital reserve fund.

### Capital Improvement Financing

Public financing will be required for all capital improvement projects. See spreadsheets for the following scenarios.

There are currently no funds available to pay the debt service on the 6-year CIP.

The anticipated debt service (assuming loans with 20-year term at 1.2% and no grants) would be approximately $2,000,000 per year after completing the 6-year CIP list.

The anticipated debt service (assuming loans with 30-year term at 1.6% and no grants) would be approximately $1,500,000 per year after completing the 6-year CIP list.

The anticipated debt service (assuming 50% grants and 50% loans, 30-year term at 1.6%) would be approximately $750,000 per year after completing the 6-year CIP list.

The anticipated debt service (assuming 75% grants and 25% loans, 30-year term at 1.6%) would be approximately $375,000 per year after completing the 6-year CIP list.

(this analysis does not include obtaining loans or ither fund from which to make debt payments)

Recommendations:

Increase sewer rates to a level at which SRF forgivable principal loan funding would be available (moderate hardship level: sewer rates = 2% of MHI). Sewer rates for Clallam Bay (MHI = $35,600) are already near this level. The MHI for Sekiu has not yet been determined; however, using Clallam County MHI ($48,000) as a stand in for Sekiu MHI, the sewer rates would need to be about $80-$90 per month for Sekiu. The combined rate for both communities should be near $75 per month.

Continue to pursue Centennial Funding grants and other grants to fund the CIP.

### Public Financing Sources

Public financing will be required for all capital improvement projects.

Maximize grant funding acquisition for CIP financing due to insufficient capacity to service added debt.